## Slide 1: Water Management Plans for Healthcare Facilities Editable Water System Process Flow Diagrams
The Centers for Disease Control and Prevention (CDC) and the American Society of Heating, Refrigerating, and Air Conditioning Engineers (ASHRAE) recommend that healthcare facilities include a water flow diagram as part of their water management plan. The following editable flow diagrams have been adapted for use from the CDC and ASHRAE. For more information on developing a water management program please visit the CDC or view the Washington State Department of Health’s seven-part video series on Legionella and Water System Management for long-term care facilities.
The sample diagrams in this document provide healthcare facilities with the ability to create a customized diagram detailed to individual facility needs. This document contains four example water flows:
Blank water flow
Basic water flow
Hazard and risk assessment flow
Monitoring and controls flow
DOH 420-270

## Slide 2: Water Management Plans for Healthcare Facilities Editable Water System Process Flow Diagrams
Instructions:
The diagrams and icons in this document are editable. Users will be able to add, delete, or edit any portion of the diagram. This includes moving arrows and boxes to customize for your specific facility.
Step 1: Right-click on the boxes that you would like to edit
Step 2: Click edit text, then type desired text
You may select and move portions of the diagram (boxes, arrows or lines) by left clicking the item and dragging it to desired location on the diagram.

## Slide 3
5. Waste
4. Hot Water Distribution
3. Heating
2. Cold Water Distribution
1. Receiving
Blank Flow Diagram
Legend:
Water Process
Backflow Preventer
Water Flow
Recirculating Return Flow
("Developing a Water Management Program to Reduce Legionella Growth and Spread in Buildings", 2017)

## Slide 4
Pool
Floor 1
Cooling Tower
(Roof)
Sinks/Showers
Floors B-11
Sanitary Sewer
Sinks/Showers
Floors B-5
Kitchen Appliances
Basement
Sinks/Showers
Floors 6-11
Hot Water Storage
Basement
Water Heater
#3:Basement Kitchen
Water Heaters
#1 & #2: Basement
Municipal Water
4” pipe from Maple St.
Hot Tub
Floor 1
Ice Machines
Floors 2,4,6,8,10
Fire Suppression
(sprinkler System)
Decorative Fountain
Lobby
5. Waste
4. Hot Water Distribution
3. Heating
2. Cold Water Distribution
1. Receiving
Basic Flow Diagram
Legend:
Water Process
Backflow Preventer
Water Flow
Recirculating Return Flow
("Developing a Water Management Program to Reduce Legionella Growth and Spread in Buildings", 2017)

## Slide 5
5. Waste
4. Hot Water Distribution
3. Heating
2. Cold Water Distribution
1. Receiving
Municipal Water
4” pipe from Maple St.
Fire Suppression
(sprinkler system)
Cooling Tower
Roof
Decorative Fountain
Lobby
Ice Machines
Floors 2,4,6,8,10
Sinks/Showers
Floors B-11
Hot Tub
Floor 1
Pool
Floor 1
Water Heaters
#1 & #2: Basement
Hot Water Storage
Basement
Water Heater
#3:Basement Kitchen
Sinks/Showers
Floors B-5
Sinks/Showers
Floors 6-11
Kitchen Appliances
Basement
Sanitary Sewer
Temperature permissive
Stagnation
No Disinfectant
Conditions for Bacteria
Spread
Special Considerations for Healthcare Facilities
External Hazards (e.g. construction, water main break)
Flow Diagram:
Hazard &
Risk Assessment
Legend:
Water Process
Backflow Preventer
Water Flow
Recirculating Return Flow
("Developing a Water Management Program to Reduce Legionella Growth and Spread in Buildings", 2017)

## Slide 6
5. Waste
4. Hot Water Distribution
3. Heating
2. Cold Water Distribution
1. Receiving
Municipal Water
4” pipe from Maple St.
Fire Suppression
(sprinkler system)
Cooling Tower
Roof
Decorative Fountain
Lobby
Ice Machines
Floors 2,4,6,8,10
Sinks/Showers
Floors B-11
Hot Tub
Floor 1
Pool
Floor 1
Water Heaters
#1 & #2: Basement
Hot Water Storage
Basement
Water Heater
#3:Basement Kitchen
Sinks/Showers
Floors B-5
Sinks/Showers
Floors 6-11
Kitchen Appliances
Basement
Sanitary Sewer
Flow Diagram: Monitoring & Controls
Visual inspection
Check Disinfectant Levels
Check Temperature
*
*
*
*
*Monitoring at representative fixtures close to and far from the central distribution point is recommended. It is not necessary to routinely monitor water conditions at every tap.
Legend:
Water Process
Backflow Preventer
Water Flow
Recirculating Return Flow
State and local regulations may exist that govern the design, construction, operation, and maintenance of public aquatic facilities (e.g., pools and tubs). INSERT LINKS
("Developing a Water Management Program to Reduce Legionella Growth and Spread in Buildings", 2017)

## Slide 7
Developing a Water Management Program to Reduce Legionella Growth and Spread in Buildings. (2019). Retrieved 5 November 2019, from https://www.cdc.gov/legionella/downloads/toolkit.pdf
ASHRAE 188: Legionellosis: Risk Management for Building Water Systems June 26, 2015. ASHRAE: Atlanta. www.ashrae.org
Resourced material provided by:
Washington State Department of Health
Office of Communicable Disease Epidemiology (206) 418-5500
Last updated: November 2019