## MOR
[6 empty] | Fluoridation Monthly Operations Report Form | [11 empty] | DOH Form 331-497 Jan. 2016
for Fluoride Acids
|  |  | System Name : | [9 empty] | System ID:
|  |  | FIP No: | [8 empty] | Month/Year:
|  |  | Contact Name: | [9 empty] | Phone #:
|  |  | Water Production |  |  |  | Fluoride Additive |  |  | Monitoring | [5 empty] | The Department of Health supports water fluoridation as a sound population-based public health measure, and supports communities in their efforts to maintain and fluoridate community water supplies.
| Date |  | Meter Reading |  | Volume Treated |  | Total Remaining (Circle one) |  | Quantity Used (Circle one) | Calculated Dosage |  |  |  | Field Tested Result*
|  |  | (MG) |  | (MG) |  | (gals) or (lbs) |  | (gals) or (lbs) | (mg/L) |  |  |  | (mg/L)
Prev.
| 1 |  |  |  | 0
| 2 |  |  |  | 0
| 3 |  |  |  | 0 | [10 empty] | Raw Water Data:
| 4 |  |  |  | 0 | [10 empty] | Date of Last Sample:
| 5 |  |  |  | 0
[16 empty] | Lab Result: |  |  |  | mg/L
| 6 |  |  |  | 0
| 7 |  |  |  | 0 | [10 empty] | Fluoride Additive Data:
| 8 |  |  |  | 0
| 9 |  |  |  | 0 | [10 empty] | Manufacturer:
| 10 |  |  |  | 0 | [10 empty] | ANSI-NSF Standard 60 Approved
| 11 |  |  |  | 0 | [10 empty] | Percent strength of acid used: |  |  |  |  | %
| 12 |  |  |  | 0 | [10 empty] | Specific Gravity (SG) of acid: |  |  |  |  | g/cm2
| 13 |  |  |  | 0
| 14 |  |  |  | 0 | [10 empty] | Testing and Monitoring:
| 15 |  |  |  | 0 | [10 empty] | *Instrument used in field testing (Make/Model)
| 16 |  |  |  | 0
Method used:
| 17 |  |  |  | 0
| 18 |  |  |  | 0
| 19 |  |  |  | 0 | [10 empty] | Weekly Instrument Calibration:
| 20 |  |  |  | 0 | [10 empty] | Date | Standard mg/L |  | Result mg/L
| 21 |  |  |  | 0
| 22 |  |  |  | 0
| 23 |  |  |  | 0
| 24 |  |  |  | 0
| 25 |  |  |  | 0
| 26 |  |  |  | 0
| 27 |  |  |  | 0 | [10 empty] | Date Split Sample Taken:
| 28 |  |  |  | 0 | [10 empty] | Split Sample Result mg/L:
| 29 |  |  |  | 0
| 30 |  |  |  | 0 | [10 empty] | Process Interuption(s) (date/time):
| 31 |  |  |  | 0 | [10 empty] | 1st Start:
| Total |  |  |  | 0 |  |  |  | 0 | [6 empty] | End:
| Min | [8 empty] | #NUM! |  |  |  | #NUM! |  | 2nd Start:
| Max | [8 empty] | 0 |  |  |  | 0 |  | End:
| Avg | [8 empty] | #DIV/0! |  |  |  | #DIV/0! |  | 3rd Start:
| Count Total | [8 empty] | 0 |  |  |  | 0 |  | End:
| Count within Range | [8 empty] | 0 |  |  |  | 0 |  | Explain cause and corrective actions taken for interruption(s) on back of page.
| Percent within Range | [8 empty] | #DIV/0! |  |  |  | #DIV/0!
Please send your report to us by the 10th day of the following month.
| Certified Operator Signature: | [14 empty] | Date:
Washington Certification No.:
If you need this publication in an alternative format, call 800.525.0127 (TDD/TTY call 711).
| This and other publications are available at: | [6 empty] | http://www.doh.wa.gov/drinkingwater
Fluoridation Monthly Operations Report - Supplemental Form
Explain cause and corrective actions taken for each interruption/overfeed.
(Use this page to the report if these occurred during the month. Add additional pages, if needed.)
|  | System Name : |  |  | 0 | [6 empty] | System ID: |  |  | 0
|  | FIP No: |  |  | 0 | [5 empty] | Month/Year: |  |  |  | 0
|  | Contact Name: |  |  | 0 | [6 empty] | Phone #: |  |  | 0
| Date(s) |  |  | Cause and Response
2016-01-01
|  | Certified Officer Signature: | [13 empty] | Date:
Please send report to: Fluoride@doh.wa.gov (preferred) OR PO BOX 47822, Olympia, WA 98504-7822 OR Fax: 360-236-2252
SPADNS
Electrode
Yes
Fluorosilicic Acid
Sodium Fluorosilicate

## Calculations
|  | Fluoridation Monthly Operations Report Form | [6 empty] | DOH Form 331-497 Jan. 2016
for Sodium Fluoride Saturators
Fluoridation Systems - Calculation for Fluorosilicic Acid and Sodium Fluorosilicate
Optimal Fluoride Level
The optimal fluoridation level for Washington State is 0.7 mg/L
Dosage
The unit of expression, milligram per liter, is used in laboratory work to indicate very small concentrations. It is a weight/volume relationship. Milligrams per liter (mg/l) and parts per million (ppm) are equivalent so long as the liquid used has a density of 1.0 grams per cubic centimeter (the density of water is 1.0). In this guidance the terms ppm and mg/l are used interchangeably. While mg/l is the preferred term, ppm is used in many instances in the interest of clarity or tradition. (Note: the term "ppm" is a unitless expression). The dosage is defined as the amount of fluoride additive needed to obtain the optimal fluoride level in the drinking water.
The dosage, expressed as milligrams per liter (mg/l) or parts per million (ppm), is obtained by subtracting the naturally occurring fluoride level from the desired fluoride level. For example, if the desired fluoride level is 0.7 mg/l and the natural fluoride level is 0.2 mg/l of the water to be fluoridated, the desired dosage will be 0.5 mg/l:
Dosage (mg/l) = Optimal level (mg/l) - Natural level(mg/l)
Dosage (mg/l) = 0.7 mg/l - 0.2mg/l
Dosage = 0.5 mg/l
Maximum Pumping Rate (Capacity)
Terms that will be used interchangeably to describe flow rate of fluoride feeders are the maximum pumping rate, plant capacity, average daily production rate, and the actual daily production.
The maximum pumping rate refers to the maximum amount of water that can be produced. The capacity of the water plant may be measured in gallons per minute (gpm), or million gallons per day (MGD). It is important to note that the sizing of a fluoride feeder is based on the maximum flow rate at the point of injection.
The daily production of water treated is determined from the daily meter readings and recorded on your Monthly Operations Report (MOR). This is recorded in millions of gallons (MG).
Here are some simple conversions:
gpm × 1440 minutes(per day) = gallons per day (gpd) | [5 empty] | gallon of water × 8.34 = pounds of water
gpd ÷ 1,000,000 = millions of gallons per day (MGD) | [5 empty] | 3785 milliliters = 1 Gallon
cubic foot (cuft) × 7.48 = gallons
Chemical Purity and Available Fluoride Ion (AFI) Concentrations
Most fluoride additives made for drinking water use are not 100% pure fluoride, so understanding the AFI is essential to obtaining the correct fluoride injection rate to optimize your fluoride program. The following chart gives the purity and AFI of the two most commonly used fluoride acid additives.
Chemical |  |  | Formula |  |  | Purity |  | Available Fluoride Ion Concentration (AFI)
Sodium Fluorosilicate |  |  | Na2SiF6 |  |  | 98.5% |  | 0.607
Fluorosilicic Acid |  |  | H2SiF6 |  |  | 23% |  | 0.792
If the AFI is multiplied by the chemical purity, the result is the amount of fluoride ion that is available after the additive is mixed in water. For example, sodium fluorosilicate contains 60.7 percent fluoride ion and has a commercial purity of 98.5% to yield 44%. Which is to say that 59.8% of the additive used is fluoride ion.
Fluoride Feed Rate
The following formula is a general equation used to calculate the concentration of an additive to water.
|  | *Fluoride Feed Rate (lb/day) = |  |  | dosage (mg/l) × capacity(MGD) × 8.34 lbs/gal
AFI × chemical purity
|  | **Fluoride Feed Rate (lb/min) = |  |  | dosage (mg/l) × capacity(gpm) × 8.34 lbs/gal
1,000,000 × AFI × chemical purity
Examples of Feed Rate Calculations:
Example 1 . A water plant produces 2,000 gpm and the city wants to add 1.1 mg/l of fluoride. What would the fluoride feed rate be?
*Fluoride Feed Rate (lb/day):
|  | 1.1 mg/l × 2.88 MGD × 8.34 lbs/gal |  |  |  |  | = 44.19 lb/day
0.607 × 0.985
The fluoride feed rate is 44.19 pounds per day. Some feed rates from equipment design data sheets are given in grams/minute. ***To convert to grams/minute, divide by 1440 minutes/day and multiply by 454 grams/pound.
***Fluoride Feed Rate (gm/min) = |  |  |  | 44.19lb/day ÷ 1440 min/day × 454 gm/lb = 13.9 gm/min
Eample 2. A water plant has a daily average production of 695 gpm and the city wants to have 0.7 mg/l fluoride level in the finished water. The natural fluoride level is than 0.1 mg/l. Find the fluoride rate using sodium fluorosilicate:
Convert the plant rate to MGD from gpm:
|  |  | 695 gpm × 1440 min/day |  |  | =1.0 MGD
1000000
*Find the fluoride feed rate:
|  | 0.7 mg/l (dosage) × 1.0 MGD (capacity) × 8.34 lbs/gal |  |  |  |  | = 9.76 lbs/day
0.607 (AFI) × 0.985 (Additive Purity)
Therefore, it takes about 10 pounds of sodium fluorosilicate to treat 1.0 MG of water to a concentration of 0.7 mg/l of fluoride.
At times, the fluoride feed must be given in cubic feet per hour. Since a cubic foot of sodium fluorosilicate weighs in the range of 75lbs.
To convert pounds per day to cubic feet per hour:
9.76 lbs per day ÷ 75 lb per ft3 ÷ 24 hrs per day = 0.00542 ft3 per hour
Example 3. If it is known that the plant rate is 4,000 gpm, the dosage needed is 0.8 mg/l, and the plant uses fluorosilicic acid, what is this the fluoride feed rate in pounds per minute?
**Find the fluoride feed rate:
|  | 0.8 mg/l (dosage) × 4000 gpm (capacity) × 8.34 lbs/gal |  |  |  |  | = 0.147 lb/min
1,000,000 × 0.79 × 0.23
A gallon of 23% fluorosilicic acid weighs 10 pounds and there are 3785 ml per gallon; thus the following following formula can be used to convert the feed rate to ml/min:
Find fluoride feed rate in ml/min:
0.147 lb/min × 10 lb/gal × 3785 ml/gal = 55.6 ml/min
4.2.7 Calculated Dosage
Washington State requires that the operators record the amount of chemical used, and that the theoretical concentration of chemical in the water be determined mathematically. In order to find the theoretical concentration of fluoride, the calculated dosage must be determined. Adding the calculated dosage to the natural fluoride level in the water supply will yield the theoretical concentration of fluoride in the water. The theoretical concentration is calculated as a safety precaution to ensure that an overfeed or accident does not occur. It is also in aid in solving trouble-shooting problems. If the theoretical concertation is significantly higher or lower than the measured concentration, steps should be taken to determine the discrepancy.
The fluoride feed rate formula for non-saturators can be changed to find the calculated dosage as follows:
|  | Dosage (mg/l) = |  | Fluoride Feed Rate (lbs/day) × AFI × Chemical Purity
Capacity (MGD) × 8.34 lbs/gal
When the fluoride Feed Rate is changed to fluoride fed and the Capacity is changed the Actual Daily Production of Water in the water system, then the dosage becomes the Calculated Dosage: the units remain the same, except that Fluoride Feed goes from lbs/day to lbs and Actual Production goes from MGD to MG.
|  | Calculated Dosage (mg/l) = |  | Fluoride Fed (lbs) × AFI × Chemical Purity
Actual production (MG) × 8.34 lbs/gal
The numerator (top) of the equation gives the pounds of fluoride ion added to the water while the denominator (bottom) gives millions of pounds of water treated. Pounds of fluoride divided by millions of water equals ppm or mg/l.
Examples of Calculated Dosage Calculation:
Example1. A plant used 65 lbs of sodium fluorosilicate to 5,540,000 gallons of water in one day. What is the calculated dosage?
Calculated Dosage (Sodium Fluorosilicate)
|  |  | 65 (lbs) × 0.607 × 0.985 |  |  | = 0.84 mg/l
5.540 (MG) × 8.34 lbs/gal
Example 2. A plant used 26 lbs of sodium fluorosilicate to 2,663,000 gallons of water in one day. What is the calculated dosage?
Calculated Dosage (Sodium Fluorosilicate)
|  |  | 26 (lbs) × 0.607 × 0.985 |  |  | = 0.70 mg/l
2.663 (MG) × 8.34 lbs/gal
Example 3. A plant used 43 lbs of Fluorosilicic Acid to 1,226,000 gallons of water in one day. Assume the acid purity is 23%. What is the calculated dosage?
Calculated Dosage (Fluorosilicic Acid)
|  |  | 43 (lbs) × 0.792 × 0.23 |  |  | = 0.77 mg/l
1.226 (MG) × 8.34 lbs/gal
Example 4. A plant used 898 lbs of Fluorosilicic Acid to 21,793,000 gallons of water in one day. Assume the acid purity is 23%. What is the calculated dosage?
Calculated Dosage (Fluorosilicic Acid)
|  |  | 898 (lbs) × 0.792 × 0.23 |  |  | = 0.90 mg/l
21.793 (MG) × 8.34 lbs/gal
Resources
* Center for Disease Control and Prevention . (1986. reprint 1991). Water Fluoridation; A Manual for Engineers and Technicians. (pp.62 - 72). Atlanta, Georgia: Reeves, Thomas G.