## Cover Page & Notes
Washington State Department of Health
Membrane Filtration Plant Monthly Report Forms
Notes and Instructions
Version 1.2
Report Designed for All Low Pressure Membrane Filtration Plants
|  |  | DOH Form | 331-517-F
|  |  | Revised | 2018-08-27
Notes:
This workbook was developed using Microsoft Excel 2000. However, it can be used in Excel 97 as well as later versions with no problems.
The workbook is intended for use by water treatment plant operators to enhance recordkeeping, reporting and legibility.
It is designed to minimize the work necessary to calculate totals, averages, count events, etc.
The SWTR Disinfection Monthly Reports will also look up and calculate required CT values for Giardia inactivation.
Data or calculations that do not comply with standards or requirements will show up in bold, italic text with pink highlighting.
Saving and Using this Workbook as a Template (Optional)
To save this workbook as a template:
Clear out any data input by the user.
Click on File, Save As. When prompted, give it a new file name, and specify the "Save as type" as Template.
Click on Save in the dialog box.
To use as template when starting a new month:
With Microsoft Excel running, click on File, New. The WTP template should show in the "New" dialog box.
Click on the template; it will come up as a regular Excel spreadsheet.
When the spreadsheet is saved for the first time, you will be required to supply a name for the file.
Recommended file name: "WTP_<PWSID>_<Plant ID>_YYMM.xls", where YYMM is the reporting year and month; e.g.: WTP_00050_001_0308.xls.
The advantage of starting a workbook using a template is that you'll always have a blank workbook (without having to clear out an old one)
and minimize the chance of overwriting a previous month's workbook.
The Forms
The workbook consists of four forms:
The Low Pressure Membrane Filtration Monthly Rept is for recording information on the operation of a low pressure membrane filtration plant.
One Membrane Filt Unit #X Form is to be used for each membrane filtration unit in operation.
The SWTR Monthly Disinfection Rept (DOH Form 331-440-F) is for recording disinfection process information for a plant using Chlorine disinfection.
The Low Pressure Membrane Monthly Summary gathers data from the other two forms, plus other provided information and reports
the SWTR compliance status for the month.
Entering Data:
All cells in the workbook are protected, except for those intended for data input by the user.
Cells and columns intended for user input have titles or headings colored blue.
Printing
Because of the size of the WTP Monthly Rept, it should be printed on legal size paper, in landscape mode, if it is desired to fit on one page.
Use the "Page Setup" menu to choose the paper size and orientation. Change left and right margins to 0.5" and check "Fit to" 1 pg wide by 1 pg tall.
The SWTR Monthly Disinfection Rept and the Monthly Summary each fit on letter size paper in landscape mode.
Where to Send these Report Forms
Send your report forms to the appropriate Office of Drinking Water regional office or as checked below:
| Northwest Drinking Water |  | Southwest Drinking Water |  | Eastern Drinking Water
| Operations |  | Operations |  | Operations
| Department of Health |  | Department of Health |  | Department of Health
| 253-395-6750 |  | 360-236-3030 |  | 509-329-2100
| dw.nwro@doh.wa.gov |  | SWTR.SWRO@doh.wa.gov |  | ero.sw.Treatment.Reports@doh.wa.gov
For Persons with Disabilities
For people with disabilities, this document is available on request in other formats. To submit a request, please call 1-800-525-0127 (TDD/TTY call 711).
Notes on Version 1.1
Added cell for turbidity standard expiration date (summary page)
Notes on Version 1.2
Updated staff contacts
Added optional template for recording required weekly verification checks of on-line turbidimeters.
Disinfection form: Added pop-up note to contact DOH if pH> 9.0 (for instructions on how to calculate CT)
Added line-by-line instructions.

## WTP Monthly Rept
Low Pressure Membrane Filtration Plant Monthly Report Form
[10 empty] | Month |  | Year
| PWS ID |  |  | PWS Name | [6 empty] | County
| Source ID |  |  | Source Name | [6 empty] | Plant ID
Cells and Columns with Blue Headings are intended for data provided by user
| Water Treated in 1000 gals | Total Hours of Operation | Filter Backwash Total in 1000 gal | Chemicals Used (lbs) | [6 empty] | Turbidity NTU |  | Combined Filter Effluent Turbidity 4 hour sample NTU | [6 empty] | No of Samples > 0.10 NTU | Max CFE Turbidity NTU | Temp C | pH |  | Total Alkalinity mg/L as CaCO3 |  | Calcium Hardness mg/L as CaCO3 Fin
Remarks
Date |  |  |  | Chlorine | ACH | Soda Ash | Citric Acid | NaOH |  |  | Raw | Settled | 1st | 2nd | 3rd | 4th | 5th | 6th | Avg |  |  | Raw | Raw | Final | Raw | Fin
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0
Max | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avg
| Total number of CFE samples analyzed for month: N = | [5 empty] | 0 | Total number of CFE samples exceeding 0.10 NTU: E = | [6 empty] | 0
| Satisfactory turbidity performance is 95% or greater. Performance determination: [1-(E/N)]x100 = | [14 empty] | Report Submitted By | [6 empty] | Signature
| Number of days CFE exceeded 1.0 NTU this month: | [5 empty] | 0 | [8 empty] | See Cover Page for information on where to send this form.
Did the CFE continuous monitoring fail to operate for more than five (5) consecutive days during this month? Y/N:

## Req'd CT Calc (hidden)
| 0 | 501 | 1001 | 2501 | 3301 |  |  |  | 0 | 6 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5 | 6.6 | 6.7 | 6.8 | 6.9 | 7 | 7.1 | 7.2 | 7.3 | 7.4 | 7.5 | 7.6 | 7.7 | 7.8 | 7.9 | 8 | 8.1 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 8.7 | 8.8 | 8.9 | 9
| 1 | 2 | 3 | 4 | 6 |  |  |  | 2 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
| PopServed | 0 |  |  | MinGrab | 1
|  |  | Inactivation Ratio Determination | [5 empty] | 0 2: Disinfection Log Reduction Req'd; 6.3 5: 0.5
Date | Peak Hour Flow gpm | Water Temp C | pH | Chlorine Residual {C} mg/L | Contact Time {T} minutes | Calculated CT {C*T} | Required CT from Tables | Inact Ratio {Calc CT/Req'd CT} | 0 2: Temp Adj; 6 2: pH Offset; 6.1 3: Chlorine Adj; 6.2 4: CT; 6.3 5: CT Calc; 6.4 6: Table Lookup; 6.5 7: CT Required; 6.6 8: Inact Ratio; 6.8 10: Lowest Daily Residual mg/L; 6.9 11: Duration less than 0.2mg/L hours; 7 12: Valid Durations hours
1 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
2 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
3 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
4 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
5 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
6 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
7 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
8 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
9 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
10 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
11 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
12 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
13 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
14 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
15 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
16 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
17 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
18 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
19 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
20 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
21 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
22 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
23 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
24 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
25 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
26 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
27 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
28 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
29 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
30 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
31 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
Total
Count | [8 empty] | 7 12: 0
Min | [8 empty] | 6.8 10: 0; 6.9 11: 0; 7 12: 0
Max | [8 empty] | 6.8 10: 0; 6.9 11: 0; 7 12: 0
Avg
| ADAM | 3
| ASOT | 3
| BENT | 3
| CHEL | 3
| CLAL | 2
| CLAR | 2
| CLIC | 3
| COLO | 3
| COLU | 3
| COWL | 2
| DOUG | 3
| FERR | 3
| FRAN | 3
| GARF | 3
| GRAN | 3
| GRAY | 2
| ILAN | 1
| ISLA | 1
| JEFF | 2
| KING | 1
| KITI | 3
| KITS | 2
| KITT | 3
| KLIC | 3
| KOWL | 2
| LEWI | 2
| LINC | 3
| MASI | 2
| MASO | 2
| OKAN | 3
| OKON | 3
| PACI | 2
| PEIR | 1
| PEND | 3
| PIER | 1
| POND | 3
| SAN | 1
| SANJ | 1
| SKAG | 1
| SKAM | 2
| SNOH | 1
| SPOK | 3
| STEV | 3
| THUR | 2
| TURS | 2
| WALL | 3
| WATC | 1
| WHAT | 1
| WHIT | 3
| WITM | 3
| YAKA | 3
| YAKI | 3

## Mem Filt Unit #1
Low Pressure Membrane Filtration Unit Monthly Report
| PWS ID | 0 |  | PWS Name | 0 |  | Month | 0 | County | 0
| Source ID | 0 |  | Source Name | 0 |  | Year | 0 | Plant ID | 0
Membrane Filtration Unit (Skid/Cell/Train) # 1
| Production |  |  | Direct Integrity Test |  |  |  | Indirect Integrity Monitoring
| Total | Flux Rate | TMP | Test Pressure | PDT | PDT | LRV | Max | Max
| Hours of | (gfd) | (psi) | (psi) | # Tests | Result | Verified | Particle Counts | Turbidity
Date | Operation | See Note 1 | See Note 2 | See Note 3 | Completed | (psi/min) | (See Note 5) | (counts/mL) | mNTU
|  | Max | Max | Min | (See Note 4) | Max | Min | See Note 6 |  | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | 0 |  |  |  | 0
Min | 0 |  | 0 | 0 | 0 |  | 0
Max | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0
Avg
| Note 1: | Maximum flux rate is _______ gfd. GFD is gallons/sq. foot/day.
| Note 2: | Maximum transmembrane pressure (TMP) is _________ psi.
| Note 3: | The minimum initial test pressure for this membrane unit is _______ psi with a ___ minute hold time.
| Note 4: | A pressure decay test (PDT) must be conducted at least once each day that the membrane filtration unit is used. An additional PDT is required if an indirect integrity threshold described in Note 6 is exceeded.
Unless the LRV is calculated and greater than the minimum required LRV of ___.0 log, the maximum allowable PDT is _______ psi/min.
| Note 5: | Calculation of the LRV is only required for those WTPs that do not operate with a fixed maximum PDT value.
The minimum required log removal value (LRV) for this WTP is ______.0 log.
| Note 6: | Either a particle counter or a laser turbidimeter is required to monitor the filtrate from each membrane filtration unit. An additional PDT is required at least once every 4 hours of operation if particle count or turbidity control limits are exceeded for 15 or more minutes.
Control limits: Particle counts - 30 counts/mL; Turbidity - 50 mNTU.
| Report Submitted By |  | 0 |  |  | WTPO Cert No |  | 0
[6 empty] | Telephone Number |  | 0

## Mem Filt Unit #2
Low Pressure Membrane Filtration Unit Monthly Report
| PWS ID | 0 |  | PWS Name | 0 |  | Month | 0 | County | 0
| Source ID | 0 |  | Source Name | 0 |  | Year | 0 | Plant ID | 0
Membrane Filtration Unit (Skid/Cell/Train) # 2
| Production |  |  | Direct Integrity Test |  |  |  | Indirect Integrity Monitoring
| Total | Flux Rate | TMP | Test Pressure | PDT | PDT | LRV | Max | Max
| Hours of | (gfd) | (psi) | (psi) | # Tests | Result | Verified | Particle Counts | Turbidity
Date | Operation | See Note 1 | See Note 2 | See Note 3 | Completed | (psi/min) | (See Note 5) | (counts/mL) | mNTU
|  | Max | Max | Min | (See Note 4) | Max | Min | See Note 6 |  | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | 0 |  |  |  | 0
Min | 0 |  | 0 | 0 | 0 |  | 0
Max | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0
Avg
| Note 1: | Maximum flux rate is _______ gfd. GFD is gallons/sq. foot/day.
| Note 2: | Maximum transmembrane pressure (TMP) is _________ psi.
| Note 3: | The minimum initial test pressure for this membrane unit is _______ psi with a ___ minute hold time.
| Note 4: | A pressure decay test (PDT) must be conducted at least once each day that the membrane filtration unit is used. An additional PDT is required if an indirect integrity threshold described in Note 6 is exceeded.
Unless the LRV is calculated and greater than the minimum required LRV of ___.0 log, the maximum allowable PDT is _______ psi/min.
| Note 5: | Calculation of the LRV is only required for those WTPs that do not operate with a fixed maximum PDT value.
The minimum required log removal value (LRV) for this WTP is ______.0 log.
| Note 6: | Either a particle counter or a laser turbidimeter is required to monitor the filtrate from each membrane filtration unit. An additional PDT is required at least once every 4 hours of operation if particle count or turbidity control limits are exceeded for 15 or more minutes.
Control limits: Particle counts - 30 counts/mL; Turbidity - 50 mNTU.
| Report Submitted By |  | 0 |  |  | WTPO Cert No |  | 0
[6 empty] | Telephone Number |  | 0

## Mem Filt Unit #3
Low Pressure Membrane Filtration Unit Monthly Report
| PWS ID | 0 |  | PWS Name | 0 |  | Month | 0 | County | 0
| Source ID | 0 |  | Source Name | 0 |  | Year | 0 | Plant ID | 0
Membrane Filtration Unit (Skid/Cell/Train) # 3
| Production |  |  | Direct Integrity Test |  |  |  | Indirect Integrity Monitoring
| Total | Flux Rate | TMP | Test Pressure | PDT | PDT | LRV | Max | Max
| Hours of | (gfd) | (psi) | (psi) | # Tests | Result | Verified | Particle Counts | Turbidity
Date | Operation | See Note 1 | See Note 2 | See Note 3 | Completed | (psi/min) | (See Note 5) | (counts/mL) | mNTU
|  | Max | Max | Min | (See Note 4) | Max | Min | See Note 6 |  | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | 0 |  |  |  | 0
Min | 0 |  | 0 | 0 | 0 |  | 0
Max | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0
Avg
| Note 1: | Maximum flux rate is _______ gfd. GFD is gallons/sq. foot/day.
| Note 2: | Maximum transmembrane pressure (TMP) is _________ psi.
| Note 3: | The minimum initial test pressure for this membrane unit is _______ psi with a ___ minute hold time.
| Note 4: | A pressure decay test (PDT) must be conducted at least once each day that the membrane filtration unit is used. An additional PDT is required if an indirect integrity threshold described in Note 6 is exceeded.
Unless the LRV is calculated and greater than the minimum required LRV of ___.0 log, the maximum allowable PDT is _______ psi/min.
| Note 5: | Calculation of the LRV is only required for those WTPs that do not operate with a fixed maximum PDT value.
The minimum required log removal value (LRV) for this WTP is ______.0 log.
| Note 6: | Either a particle counter or a laser turbidimeter is required to monitor the filtrate from each membrane filtration unit. An additional PDT is required at least once every 4 hours of operation if particle count or turbidity control limits are exceeded for 15 or more minutes.
Control limits: Particle counts - 30 counts/mL; Turbidity - 50 mNTU.
| Report Submitted By |  | 0 |  |  | WTPO Cert No |  | 0
[6 empty] | Telephone Number |  | 0

## Mem Filt Unit #4
Low Pressure Membrane Filtration Unit Monthly Report
| PWS ID | 0 |  | PWS Name | 0 |  | Month | 0 | County | 0
| Source ID | 0 |  | Source Name | 0 |  | Year | 0 | Plant ID | 0
Membrane Filtration Unit (Skid/Cell/Train) # 4
| Production |  |  | Direct Integrity Test |  |  |  | Indirect Integrity Monitoring
| Total | Flux Rate | TMP | Test Pressure | PDT | PDT | LRV | Max | Max
| Hours of | (gfd) | (psi) | (psi) | # Tests | Result | Verified | Particle Counts | Turbidity
Date | Operation | See Note 1 | See Note 2 | See Note 3 | Completed | (psi/min) | (See Note 5) | (counts/mL) | mNTU
|  | Max | Max | Min | (See Note 4) | Max | Min | See Note 6 |  | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | 0 |  |  |  | 0
Min | 0 |  | 0 | 0 | 0 |  | 0
Max | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0
Avg
| Note 1: | Maximum flux rate is _______ gfd. GFD is gallons/sq. foot/day.
| Note 2: | Maximum transmembrane pressure (TMP) is _________ psi.
| Note 3: | The minimum initial test pressure for this membrane unit is _______ psi with a ___ minute hold time.
| Note 4: | A pressure decay test (PDT) must be conducted at least once each day that the membrane filtration unit is used. An additional PDT is required if an indirect integrity threshold described in Note 6 is exceeded.
Unless the LRV is calculated and greater than the minimum required LRV of ___.0 log, the maximum allowable PDT is _______ psi/min.
| Note 5: | Calculation of the LRV is only required for those WTPs that do not operate with a fixed maximum PDT value.
The minimum required log removal value (LRV) for this WTP is ______.0 log.
| Note 6: | Either a particle counter or a laser turbidimeter is required to monitor the filtrate from each membrane filtration unit. An additional PDT is required at least once every 4 hours of operation if particle count or turbidity control limits are exceeded for 15 or more minutes.
Control limits: Particle counts - 30 counts/mL; Turbidity - 50 mNTU.
| Report Submitted By |  | 0 |  |  | WTPO Cert No |  | 0
[6 empty] | Telephone Number |  | 0

## Online Turb Verification
Weekly Verification Checks-Online Turbidimeters
PWS Name | 0
PWS ID | 0
WEEK 1 (date): |  | Operator Name: |  |  |  | WEEK 2 (date): |  | Operator Name:
Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action | Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action
Example: IFE-FILTER #1/HACH 1720E | 0.08 | 0.08 | 0.09 | Y | none | Example: CFE/HACH 1720E | 0.13 | 0.14 | 0.05 | N | Recalibrated on-line
|  |  |  | * or 10% for the raw | [5 empty] | * or 10% for the raw
WEEK 3 (date): |  | Operator Name: |  |  |  | WEEK 4 (date): |  | Operator Name:
Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action | Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action
* or 10% for the raw
WEEK 5 (date): |  | Operator Name:
Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action
* or 10% for the raw

## SWTR Monthly Disinfection Rept
Washington State Department of Health
SWTR Disinfection Monthly Report Form
| PWS ID | 0 |  | PWS Name | 0 |  |  |  | Month | 0 | Year | 0
| County | 0 | [5 empty] | Submitted By |  | 0
| Source ID | 0 |  | Source Name | 0 |  | . | WTPO Cert No |  | 0
| Plant ID | 0 | [5 empty] | Telephone No |  | 0
Population Served |  |  |  |  | Min Grab Samples Reqd | 1 | Residuals Normally Measured Continuously Y/N |  |  |  | Y
Overall Log Treatment Req'd |  |  | 3 |  | Filtration Log Removal Credit |  |  | 3 |  | Required Disinfection Log Reduction |  |  |  | 0.5
Cells and Columns with Blue Headings are intended for data provided by user
|  |  | Inactivation Ratio Determination | [7 empty] | Disinfectant Residual at |  |  | Residual in
Note: For correct results, remember to enter your plant's Filtration Log Removal Credit in cell I9 above | [10 empty] | Distribution Entry Point |  |  | Distribution System
Date | Peak Hour Flow gpm | Water Temp C | pH | Chlorine Residual {C} mg/L | Tank level ft (must be at least __ ft) | Contact Time {T} minutes | Calculated CT {C*T} | Required CT from Tables* | Inact Ratio {Calc CT/Req'd CT} | No. of Samples Collected "C" if Continuous | Lowest Daily Residual mg/L | Duration less than 0.2mg/L hours | DOH Notified? Name & Time | No of Sites Sampled | Minimum Residual mg/L | No of Samples Residual Not Detected
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | [9 empty] | 0 | # < 0.2 mg/L | # > 4 hrs |  | 0 |  | 0
Count | [8 empty] | 0 |  | 0 | 0
Min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0
Max | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0
Avg
| *Adjusted for Log Reduction Required |  |  |  |  | No. Days Inact Ratio < 1 |  | 0
DOH Form 331-440-F (Excel version) |  |  |  | Notes: | [5 empty] | Signature

## Monthly Summary
Low Pressure Membrane Filtration Plant
Monthly Report Summary Form
PWS ID | 0 |  | Source ID | 0 |  |  | Month | 0 | Year | 0
PWS Name | 0 |  |  | Source Name |  | 0
|  |  |  | Plant ID | 0 |  |  | County | 0
| Color code: | WTP Monthly Rept |  | Mem Filt Unit Rprts |  | SWTR Monthly Disinfection Rept |  |  | Supplied by you
Source (Raw) Water | 7. Maximum density of raw water fecal coliform (# organisms/100 ml)
| 8. Number of days raw water turbidity was monitored this month | [7 empty] | 0
| 9. Maximum turbidity of the raw water treated by the plant (NTU) | [7 empty] | 0
Filtration | 10. Hours of operation during reporting month | [7 empty] | 0
| 11. Number of filtered water turbidity measurements taken | [7 empty] | 0
| 12. Turbidity performance limit |  |  | No. of filtered measurements > performance limit |  |  |  |  | 0
| 13. Max. allowable turbidity |  |  | No. of days finished water measurements > max allowable limit: |  |  |  |  | 0
| 14. Maximum filtered water turbidity (NTU) | [7 empty] | 0
| 15. Was unfiltered water provided to consumers at any time? | [6 empty] | Y/N:
| 16. Approved maximum TMP (psi): | [6 empty] | Max operational TMP (psi): | 0
| 17. Approved maximum pressure decay rate (psi/min): | [6 empty] | Max pressure decay rate (psi/min): | 0
| 18. Minimum calculated Cryptosporidium log removal value: | [6 empty] | NA or : | NA
19. Number of direct integrity tests failing the criteria (Line # 17):
20. Number of times indirect integrity (particle counts or laser turbidity) control limit exceeded:
| 21. Approved maximum flux rate (gpd/sq ft): | [6 empty] | Maximum operational flux rate (gpd/sq ft): | 0
| 22. Maximum flow rate treated (gpm): | [7 empty] | 0
Inactivation Ratio | 23. Number of days disinfectant CT was monitored this month | [7 empty] | 0
| 24. Number of days inactivation ratio was below 1.0 (Enter 0 if none) | [7 empty] | 0
| 25. Lowest inactivation ratio achieved | [7 empty] | 0
Distribution Entry Point Samples | 26. Number of days during which plant produced water during month | [7 empty] | 0
| 27. Number of entry point residual samples analyzed during month | [7 empty] | 0
| 28. No of days when residual fell below 0.2 mg/l (Enter 0 if none) | [7 empty] | 0
| 29. No of days when residual fell below 0.2 mg/l for more than 4 hours (Enter 0 if none) | [7 empty] | 0
Distribution System Residuals | 30. Number of days water served to public this month
31. Number of days distribution system disinfectant residual was monitored
| 32. No of distribution system disinfectant residual samples measured this month | [7 empty] | 0
| 33. No of samples where no disinfectant residual was detected (Enter 0 if none) | [7 empty] | 0
34. Average of all disinfectant residual measurements taken with coliform samples
Finished Water/ General | 35. Number of water quality complaints received from consumers served by system
| 36. Did certified operator take all req'd pH, temp, turbidity, and residual disinfectant conc? | [6 empty] | Y/N:
| 37. Were all turbidimeters calibrated w/ primary standard within last quarter? Date | [6 empty] | Y/N:
Primary standard expiration date:
| 38. Critical alarms tested? Remarks: |  |  |  |  | Date |  | Y/N:
Report Submitted By | [5 empty] | WTPO Cert No
Signature | [5 empty] | Telephone Number
See Cover Page for information on where to send this form.

## Line-by-line instructions
Line-by-Line Instructions
General Reminder: Cells and columns intended for user input have titles or headings colored blue.
WTP Monthly Rept
Column | Comment
Water Treated (1000 gal) | Automatically calculated from meter readings. Include all water treated, including filter-to-waste.
Total Hours of Operation | You can determine this using SCADA, a chart recorder, a plant run time meter, or estimate using the total volume produced divided by the known (fixed) plant flow rate
Chlorine Used (lbs) | (liquid) lbs/day=lbs/gal x gal/day lbs/gal=(% Solution/100) x 8.34 lbs/gal x specific gravity
Turbidity Raw | If monitoring continuously, record the daily average value. If using grab samples, collect representative sample(s) daily.
Remarks | Record anything unusual or out-of-the-ordinary here.
Online Turb Verification
Use this template to record the required weekly verification checks of your online turbidimeters. You do not need to use it if you already have a system in place to record the information. Keep this on file. It is not necessary to submit it unless the department requests it.
SWTR Monthly Disinfection Report
Column | Comment
Peak hourly flow (PHF) | This is the maximum one-hour flow through the contact basin, expressed in gallons per minute. It is not the peak instantaneous flow. Use the flow into or out of the contact basin, whichever is higher. For most systems, this is the flow leaving the contact basin.
Water temperature | Measure during PHF at the same location as chlorine residual (for CT). May also report daily minimum if you have continuous measurement.
pH | Measure during PHF at the same location as chlorine residual (for CT). May also report daily maximum if you have continuous measurement. Call your DOH regional office for instructions if your pH exceeds 9.0
Chlorine Residual (CT) | Measure the free chlorine residual at the end of the contact basin or pipe, prior to the first customer, during PHF. May also report daily minimum if you have continuous measurement.
Tank Level | If you use a storage tank or clearwell for contact time, record the tank level during peak hourly flow. May also report the daily minimum tank level. In the column header, record the assumed minimum tank level, if any, used for your CT calculation.
Contact Time | Calculate this every day (not at the end of the month). Use PHF and your DOH-approved CT calculation.
Inact Ratio | This calculates automatically based on the numbers you enter. Call your DOH regional office immediately if the value drops below 1.0
Entry Point-Lowest Daily Residual mg/L | Systems serving more than 3300 people must monitor continuously & report the lowest absolute value for the day. If continuous equipment fails, you must take grab samples every four hours and have equipment back up and running with five working days. Systems serving less than 3300 people may use grab samples (1-4 per day depending on population) Systems using grab sampling, take one sample at PHF and the remaining samples spaced over the period that the plant produces water. Record the lowest grab sample result. Call your DOH regional office immediately if this value drops below 0.2 mg/L
Entry Point-Duration less than 0.2 mg/L hours | Enter the total length of time that the residual was below 0.2 mg/L.
DOH Notified? Name & Time | Each day the residual was below 0.2 mg/L write the date and the name of the person you reported to at DOH
Distribution-No of Sites Sampled | Measure distribution residual at least once per day and at the same time and location as coliform samples. Measure from representative locations throughout the distribution system.
Minimum Residual mg/L | Record the lowest free chlorine residual for the day. Systems using chloramines: record the combined chlorine residual.
No of Samples Residual Not Detected | Systems that use heterotrophic plate counts (HPC): an HPC level less than or equal to 500 organisms/mL is considered to have a detectable residual disinfectant concentration. For systems that do not use HPC, "detectable residual disinfectant concentration" means 0.2 mg/L free chlorine, total chlorine or combined chlorine. The department may approve a written request to use a lower value. At a minimum, the request to use a lower value must identify the instrument used to measure the residual disinfectant concentration and include the manufacturer's documentation on the instrument's accuracy to measure the lower value.
Monthly Summary
All blanks must be completed each month. If a question does not apply to your system, please check the n/a box.
Item # | Comment
7 | WAC 246-290-664(1)
9 | Maximum raw water turbidity-Maximum of the reported daily values for the month. (populates automatically)
11 | Filtered water turbidity measurements reported for the combined filter effluent from the treatment plant. (populates automatically)
12 & 13 | Turbidity performance limit is the 95th percentile limit, the maximum allowable limit is the limit “never to exceed.” Enter the specific limits approved for your plant in the spaces provided.
15 | Specifically, was any unfiltered surface water or GWI water provided, not from an alternate source such as wells.
16 | Enter the specific limit approved for your plant in the space provided. Report values as positive values (in psi) whether you are referring to pressure or vacuum differentials.
17 | Some membrane filtration plants operate with a fixed maximum pressure decay rate. If your plant operates in this way, enter the approved maximum value. Otherwise enter “NA” for the approved value. All plants must enter the maximum pressure decay rate observed during direct integrity testing.
18 | Some membrane filtration plants operate using a state approved mathematical formula to continuously calculate the Cryptosporidium log removal provided. Others operate with a fixed maximum pressure decay rate. Enter a value only if your plant operates with a state approved mathematical formula to calculate a log removal value (LRV). Otherwise, check N/A.
20 | All membrane filtration units must have continuous indirect integrity monitoring equipment, either a laser turbidimeter or particle counter. Only record those times during which the control limit was exceeded for 15 or more minutes.
21 | Enter the maximum flux rate approved for your plant. If the flux rate is not restricted, enter “NR”.
33 | Disinfectant Residuals - A heterotrophic plate count (HPC) level less than or equal to 500 organisms/mL is considered to have a detectable residual disinfectant concentration.
34 | This question is to help meet a DBP rule requirement: systems must measure and report the average value each month of the residual disinfectant level at the same time/location as coliform samples. Subpart H (surface water) systems have the option of using the results of the daily distribution samples - this option should be specified in your DBP monitoring plan. If you opted to use the daily distribution samples, enter that average here.
36 | Analytical Measurements - Only qualified persons (such as certified operators) shall conduct measurements for pH, temperature, turbidity, and residual disinfectant concentrations. See WAC 246-290-638(1) for details.
37 | Turbidimeter Calibration - Calibrate turbidity equipment based upon a primary standard on at least a quarterly basis for instruments using an incandescent light source and on at least an annual basis for instruments using an LED or laser light source. If there are more than one and they were calibrated on different dates, enter the earliest calibration date. WAC 246-290-638(4)
38 | Critical alarms are those alarms that monitor a critical treatment process such as filtration or disinfection where treatment failure poses an immediate risk to public health and/or safety. For plants that run in an unattended mode, these alarms must trigger plant shutdown, not just dial out to the on-call operator. Recommended testing frequency: Plants staffed 24/7 (quarterly), Plants that operate some of the time unattended (monthly), Plants with a history of reliability problems (weekly)
Signature | The operator in responsible charge with the appropriate level of certification (at or above the plant rating) must sign this form.

## CT Lookup Table
Look-up Table for Required CT for 1 log Reduction in Giardia at Various Temperatures, Chlorine Concentration and pH
Temp | Chlorine | Lookup | [6 empty] | pH | [17 empty] | pH
Degrees | Conc | Row
C | (mg/l) |  | 6 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5 | 6.6 | 6.7 | 6.8 | 6.9 | 7 | 7.1 | 7.2 | 7.3 | 7.4 | 7.5 | 7.6 | 7.7 | 7.8 | 7.9 | 8 | 8.1 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 8.7 | 8.8 | 8.9 | 9
0 | 0 | 0 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0 | 500 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0.4 | 504 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0.6 | 506 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.6 | 72.2 | 74.8 | 77.4 | 80 | 83 | 86 | 89 | 92 | 95 | 98.8 | 102.6 | 106.4 | 110.2 | 114 | 118.4 | 122.8 | 127.2 | 131.6 | 136
0.5 | 0.8 | 508 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.8 | 73.6 | 76.4 | 79.2 | 82 | 85.2 | 88.4 | 91.6 | 94.8 | 98 | 102 | 106 | 110 | 114 | 118 | 122.6 | 127.2 | 131.8 | 136.4 | 141
0.5 | 1 | 510 | 49 | 51 | 53 | 55 | 57 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.4 | 90.8 | 94.2 | 97.6 | 101 | 105.2 | 109.4 | 113.6 | 117.8 | 122 | 126.8 | 131.6 | 136.4 | 141.2 | 146
0.5 | 1.2 | 512 | 51 | 52.8 | 54.6 | 56.4 | 58.2 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86 | 89.6 | 93.2 | 96.8 | 100.4 | 104 | 108.2 | 112.4 | 116.6 | 120.8 | 125 | 130 | 135 | 140 | 145 | 150
0.5 | 1.4 | 514 | 52 | 53.8 | 55.6 | 57.4 | 59.2 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.6 | 96.2 | 99.8 | 103.4 | 107 | 111.4 | 115.8 | 120.2 | 124.6 | 129 | 134.2 | 139.4 | 144.6 | 149.8 | 155
0.5 | 1.6 | 516 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63 | 65.4 | 67.8 | 70.2 | 72.6 | 75 | 78.2 | 81.4 | 84.6 | 87.8 | 91 | 94.8 | 98.6 | 102.4 | 106.2 | 110 | 114.4 | 118.8 | 123.2 | 127.6 | 132 | 137.4 | 142.8 | 148.2 | 153.6 | 159
0.5 | 1.8 | 518 | 54 | 56 | 58 | 60 | 62 | 64 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 80.2 | 83.4 | 86.6 | 89.8 | 93 | 97 | 101 | 105 | 109 | 113 | 117.6 | 122.2 | 126.8 | 131.4 | 136 | 141.4 | 146.8 | 152.2 | 157.6 | 163
0.5 | 2 | 520 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 82.2 | 85.4 | 88.6 | 91.8 | 95 | 99 | 103 | 107 | 111 | 115 | 119.8 | 124.6 | 129.4 | 134.2 | 139 | 144.6 | 150.2 | 155.8 | 161.4 | 167
0.5 | 2.2 | 522 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.6 | 88.2 | 91.8 | 95.4 | 99 | 102.8 | 106.6 | 110.4 | 114.2 | 118 | 122.8 | 127.6 | 132.4 | 137.2 | 142 | 147.6 | 153.2 | 158.8 | 164.4 | 170
0.5 | 2.4 | 524 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.8 | 73.6 | 76.4 | 79.2 | 82 | 85.4 | 88.8 | 92.2 | 95.6 | 99 | 103.2 | 107.4 | 111.6 | 115.8 | 120 | 125 | 130 | 135 | 140 | 145 | 150.8 | 156.6 | 162.4 | 168.2 | 174
0.5 | 2.6 | 526 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.4 | 90.8 | 94.2 | 97.6 | 101 | 105.4 | 109.8 | 114.2 | 118.6 | 123 | 128 | 133 | 138 | 143 | 148 | 154 | 160 | 166 | 172 | 178
0.5 | 2.8 | 528 | 59 | 61.4 | 63.8 | 66.2 | 68.6 | 71 | 74 | 77 | 80 | 83 | 86 | 89.4 | 92.8 | 96.2 | 99.6 | 103 | 107.4 | 111.8 | 116.2 | 120.6 | 125 | 130.2 | 135.4 | 140.6 | 145.8 | 151 | 157 | 163 | 169 | 175 | 181
0.5 | 3 | 530 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 75 | 78 | 81 | 84 | 87 | 90.6 | 94.2 | 97.8 | 101.4 | 105 | 109.4 | 113.8 | 118.2 | 122.6 | 127 | 132.2 | 137.4 | 142.6 | 147.8 | 153 | 159.2 | 165.4 | 171.6 | 177.8 | 184
1 | 0 | 1000 | 44.4444 | 46.0222 | 47.6 | 49.1778 | 50.7556 | 52.3333 | 54.4444 | 56.5556 | 58.6667 | 60.7778 | 62.8889 | 65.5778 | 68.2667 | 70.9556 | 73.6444 | 76.3333 | 78.8889 | 81.4444 | 84 | 86.5556 | 89.1111 | 92.6 | 96.0889 | 99.5778 | 103.0667 | 106.5556 | 110.4222 | 114.2889 | 118.1556 | 122.0222 | 125.8889
1 | 0.4 | 1004 | 44.4444 | 46.0222 | 47.6 | 49.1778 | 50.7556 | 52.3333 | 54.4444 | 56.5556 | 58.6667 | 60.7778 | 62.8889 | 65.5778 | 68.2667 | 70.9556 | 73.6444 | 76.3333 | 78.8889 | 81.4444 | 84 | 86.5556 | 89.1111 | 92.6 | 96.0889 | 99.5778 | 103.0667 | 106.5556 | 110.4222 | 114.2889 | 118.1556 | 122.0222 | 125.8889
1 | 0.6 | 1006 | 45.4444 | 47.2 | 48.9556 | 50.7111 | 52.4667 | 54.2222 | 56.3556 | 58.4889 | 60.6222 | 62.7556 | 64.8889 | 67.4 | 69.9111 | 72.4222 | 74.9333 | 77.4444 | 80.3556 | 83.2667 | 86.1778 | 89.0889 | 92 | 95.6667 | 99.3333 | 103 | 106.6667 | 110.3333 | 114.6 | 118.8667 | 123.1333 | 127.4 | 131.6667
1 | 0.8 | 1008 | 46.4444 | 48.2 | 49.9556 | 51.7111 | 53.4667 | 55.2222 | 57.3556 | 59.4889 | 61.6222 | 63.7556 | 65.8889 | 68.5778 | 71.2667 | 73.9556 | 76.6444 | 79.3333 | 82.4444 | 85.5556 | 88.6667 | 91.7778 | 94.8889 | 98.7556 | 102.6222 | 106.4889 | 110.3556 | 114.2222 | 118.6667 | 123.1111 | 127.5556 | 132 | 136.4444
1 | 1 | 1010 | 47.4444 | 49.3778 | 51.3111 | 53.2444 | 55.1778 | 57.1111 | 59.2444 | 61.3778 | 63.5111 | 65.6444 | 67.7778 | 70.4889 | 73.2 | 75.9111 | 78.6222 | 81.3333 | 84.6222 | 87.9111 | 91.2 | 94.4889 | 97.7778 | 101.8444 | 105.9111 | 109.9778 | 114.0444 | 118.1111 | 122.7556 | 127.4 | 132.0444 | 136.6889 | 141.3333
1 | 1.2 | 1012 | 49.3333 | 51.0667 | 52.8 | 54.5333 | 56.2667 | 58 | 60.3333 | 62.6667 | 65 | 67.3333 | 69.6667 | 72.3778 | 75.0889 | 77.8 | 80.5111 | 83.2222 | 86.7111 | 90.2 | 93.6889 | 97.1778 | 100.6667 | 104.7333 | 108.8 | 112.8667 | 116.9333 | 121 | 125.8444 | 130.6889 | 135.5333 | 140.3778 | 145.2222
1 | 1.4 | 1014 | 50.2222 | 51.9778 | 53.7333 | 55.4889 | 57.2444 | 59 | 61.5111 | 64.0222 | 66.5333 | 69.0444 | 71.5556 | 74.4444 | 77.3333 | 80.2222 | 83.1111 | 86 | 89.5111 | 93.0222 | 96.5333 | 100.0444 | 103.5556 | 107.8 | 112.0444 | 116.2889 | 120.5333 | 124.7778 | 129.8222 | 134.8667 | 139.9111 | 144.9556 | 150
1 | 1.6 | 1016 | 50.3333 | 52.4444 | 54.5556 | 56.6667 | 58.7778 | 60.8889 | 63.2222 | 65.5556 | 67.8889 | 70.2222 | 72.5556 | 75.6444 | 78.7333 | 81.8222 | 84.9111 | 88 | 91.6667 | 95.3333 | 99 | 102.6667 | 106.3333 | 110.6222 | 114.9111 | 119.2 | 123.4889 | 127.7778 | 132.9778 | 138.1778 | 143.3778 | 148.5778 | 153.7778
1 | 1.8 | 1018 | 52.2222 | 54.1556 | 56.0889 | 58.0222 | 59.9556 | 61.8889 | 64.4 | 66.9111 | 69.4222 | 71.9333 | 74.4444 | 77.5333 | 80.6222 | 83.7111 | 86.8 | 89.8889 | 93.7556 | 97.6222 | 101.4889 | 105.3556 | 109.2222 | 113.6889 | 118.1556 | 122.6222 | 127.0889 | 131.5556 | 136.7778 | 142 | 147.2222 | 152.4444 | 157.6667
1 | 2 | 1020 | 53.2222 | 55.3333 | 57.4444 | 59.5556 | 61.6667 | 63.7778 | 66.2889 | 68.8 | 71.3111 | 73.8222 | 76.3333 | 79.4444 | 82.5556 | 85.6667 | 88.7778 | 91.8889 | 95.7556 | 99.6222 | 103.4889 | 107.3556 | 111.2222 | 115.8667 | 120.5111 | 125.1556 | 129.8 | 134.4444 | 139.8667 | 145.2889 | 150.7111 | 156.1333 | 161.5556
1 | 2.2 | 1022 | 54.1111 | 56.2444 | 58.3778 | 60.5111 | 62.6444 | 64.7778 | 67.4667 | 70.1556 | 72.8444 | 75.5333 | 78.2222 | 81.6889 | 85.1556 | 88.6222 | 92.0889 | 95.5556 | 99.2667 | 102.9778 | 106.6889 | 110.4 | 114.1111 | 118.7556 | 123.4 | 128.0444 | 132.6889 | 137.3333 | 142.7556 | 148.1778 | 153.6 | 159.0222 | 164.4444
1 | 2.4 | 1024 | 55.1111 | 57.2444 | 59.3778 | 61.5111 | 63.6444 | 65.7778 | 68.4667 | 71.1556 | 73.8444 | 76.5333 | 79.2222 | 82.5333 | 85.8444 | 89.1556 | 92.4667 | 95.7778 | 99.8222 | 103.8667 | 107.9111 | 111.9556 | 116 | 120.8444 | 125.6889 | 130.5333 | 135.3778 | 140.2222 | 145.8444 | 151.4667 | 157.0889 | 162.7111 | 168.3333
1 | 2.6 | 1026 | 56.1111 | 58.4222 | 60.7333 | 63.0444 | 65.3556 | 67.6667 | 70.3556 | 73.0444 | 75.7333 | 78.4222 | 81.1111 | 84.4222 | 87.7333 | 91.0444 | 94.3556 | 97.6667 | 101.9111 | 106.1556 | 110.4 | 114.6444 | 118.8889 | 123.7333 | 128.5778 | 133.4222 | 138.2667 | 143.1111 | 148.9111 | 154.7111 | 160.5111 | 166.3111 | 172.1111
1 | 2.8 | 1028 | 57 | 59.3111 | 61.6222 | 63.9333 | 66.2444 | 68.5556 | 71.4444 | 74.3333 | 77.2222 | 80.1111 | 83 | 86.3111 | 89.6222 | 92.9333 | 96.2444 | 99.5556 | 103.8222 | 108.0889 | 112.3556 | 116.6222 | 120.8889 | 125.9111 | 130.9333 | 135.9556 | 140.9778 | 146 | 151.8 | 157.6 | 163.4 | 169.2 | 175
1 | 3 | 1030 | 58 | 60.3111 | 62.6222 | 64.9333 | 67.2444 | 69.5556 | 72.4667 | 75.3778 | 78.2889 | 81.2 | 84.1111 | 87.6 | 91.0889 | 94.5778 | 98.0667 | 101.5556 | 105.8 | 110.0444 | 114.2889 | 118.5333 | 122.7778 | 127.8222 | 132.8667 | 137.9111 | 142.9556 | 148 | 154 | 160 | 166 | 172 | 178
2 | 0 | 2000 | 41.3333 | 42.8667 | 44.4 | 45.9333 | 47.4667 | 49 | 50.9333 | 52.8667 | 54.8 | 56.7333 | 58.6667 | 61.1333 | 63.6 | 66.0667 | 68.5333 | 71 | 73.4667 | 75.9333 | 78.4 | 80.8667 | 83.3333 | 86.6 | 89.8667 | 93.1333 | 96.4 | 99.6667 | 103.2667 | 106.8667 | 110.4667 | 114.0667 | 117.6667
2 | 0.4 | 2004 | 41.3333 | 42.8667 | 44.4 | 45.9333 | 47.4667 | 49 | 50.9333 | 52.8667 | 54.8 | 56.7333 | 58.6667 | 61.1333 | 63.6 | 66.0667 | 68.5333 | 71 | 73.4667 | 75.9333 | 78.4 | 80.8667 | 83.3333 | 86.6 | 89.8667 | 93.1333 | 96.4 | 99.6667 | 103.2667 | 106.8667 | 110.4667 | 114.0667 | 117.6667
2 | 0.6 | 2006 | 42.3333 | 44 | 45.6667 | 47.3333 | 49 | 50.6667 | 52.6667 | 54.6667 | 56.6667 | 58.6667 | 60.6667 | 63 | 65.3333 | 67.6667 | 70 | 72.3333 | 75.0667 | 77.8 | 80.5333 | 83.2667 | 86 | 89.4 | 92.8 | 96.2 | 99.6 | 103 | 107 | 111 | 115 | 119 | 123
2 | 0.8 | 2008 | 43.3333 | 45 | 46.6667 | 48.3333 | 50 | 51.6667 | 53.6667 | 55.6667 | 57.6667 | 59.6667 | 61.6667 | 64.1333 | 66.6 | 69.0667 | 71.5333 | 74 | 76.9333 | 79.8667 | 82.8 | 85.7333 | 88.6667 | 92.2667 | 95.8667 | 99.4667 | 103.0667 | 106.6667 | 110.8 | 114.9333 | 119.0667 | 123.2 | 127.3333
2 | 1 | 2010 | 44.3333 | 46.1333 | 47.9333 | 49.7333 | 51.5333 | 53.3333 | 55.3333 | 57.3333 | 59.3333 | 61.3333 | 63.3333 | 65.8667 | 68.4 | 70.9333 | 73.4667 | 76 | 79.0667 | 82.1333 | 85.2 | 88.2667 | 91.3333 | 95.1333 | 98.9333 | 102.7333 | 106.5333 | 110.3333 | 114.6667 | 119 | 123.3333 | 127.6667 | 132
2 | 1.2 | 2012 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.5333 | 70.0667 | 72.6 | 75.1333 | 77.6667 | 80.9333 | 84.2 | 87.4667 | 90.7333 | 94 | 97.8 | 101.6 | 105.4 | 109.2 | 113 | 117.5333 | 122.0667 | 126.6 | 131.1333 | 135.6667
2 | 1.4 | 2014 | 46.6667 | 48.3333 | 50 | 51.6667 | 53.3333 | 55 | 57.3333 | 59.6667 | 62 | 64.3333 | 66.6667 | 69.3333 | 72 | 74.6667 | 77.3333 | 80 | 83.3333 | 86.6667 | 90 | 93.3333 | 96.6667 | 100.6 | 104.5333 | 108.4667 | 112.4 | 116.3333 | 121.0667 | 125.8 | 130.5333 | 135.2667 | 140
2 | 1.6 | 2016 | 47 | 48.9333 | 50.8667 | 52.8 | 54.7333 | 56.6667 | 58.8667 | 61.0667 | 63.2667 | 65.4667 | 67.6667 | 70.5333 | 73.4 | 76.2667 | 79.1333 | 82 | 85.4 | 88.8 | 92.2 | 95.6 | 99 | 103.0667 | 107.1333 | 111.2 | 115.2667 | 119.3333 | 124.1333 | 128.9333 | 133.7333 | 138.5333 | 143.3333
2 | 1.8 | 2018 | 48.6667 | 50.4667 | 52.2667 | 54.0667 | 55.8667 | 57.6667 | 60 | 62.3333 | 64.6667 | 67 | 69.3333 | 72.2 | 75.0667 | 77.9333 | 80.8 | 83.6667 | 87.2667 | 90.8667 | 94.4667 | 98.0667 | 101.6667 | 105.8667 | 110.0667 | 114.2667 | 118.4667 | 122.6667 | 127.5333 | 132.4 | 137.2667 | 142.1333 | 147
2 | 2 | 2020 | 49.6667 | 51.6 | 53.5333 | 55.4667 | 57.4 | 59.3333 | 61.6667 | 64 | 66.3333 | 68.6667 | 71 | 73.9333 | 76.8667 | 79.8 | 82.7333 | 85.6667 | 89.2667 | 92.8667 | 96.4667 | 100.0667 | 103.6667 | 108 | 112.3333 | 116.6667 | 121 | 125.3333 | 130.4 | 135.4667 | 140.5333 | 145.6 | 150.6667
2 | 2.2 | 2022 | 50.3333 | 52.3333 | 54.3333 | 56.3333 | 58.3333 | 60.3333 | 62.8 | 65.2667 | 67.7333 | 70.2 | 72.6667 | 75.8667 | 79.0667 | 82.2667 | 85.4667 | 88.6667 | 92.2 | 95.7333 | 99.2667 | 102.8 | 106.3333 | 110.6667 | 115 | 119.3333 | 123.6667 | 128 | 133.0667 | 138.1333 | 143.2 | 148.2667 | 153.3333
2 | 2.4 | 2024 | 51.3333 | 53.3333 | 55.3333 | 57.3333 | 59.3333 | 61.3333 | 63.8 | 66.2667 | 68.7333 | 71.2 | 73.6667 | 76.8 | 79.9333 | 83.0667 | 86.2 | 89.3333 | 93.0667 | 96.8 | 100.5333 | 104.2667 | 108 | 112.5333 | 117.0667 | 121.6 | 126.1333 | 130.6667 | 135.9333 | 141.2 | 146.4667 | 151.7333 | 157
2 | 2.6 | 2026 | 52.3333 | 54.4667 | 56.6 | 58.7333 | 60.8667 | 63 | 65.4667 | 67.9333 | 70.4 | 72.8667 | 75.3333 | 78.4667 | 81.6 | 84.7333 | 87.8667 | 91 | 94.9333 | 98.8667 | 102.8 | 106.7333 | 110.6667 | 115.2 | 119.7333 | 124.2667 | 128.8 | 133.3333 | 138.7333 | 144.1333 | 149.5333 | 154.9333 | 160.3333
2 | 2.8 | 2028 | 53 | 55.1333 | 57.2667 | 59.4 | 61.5333 | 63.6667 | 66.3333 | 69 | 71.6667 | 74.3333 | 77 | 80.1333 | 83.2667 | 86.4 | 89.5333 | 92.6667 | 96.6667 | 100.6667 | 104.6667 | 108.6667 | 112.6667 | 117.3333 | 122 | 126.6667 | 131.3333 | 136 | 141.4 | 146.8 | 152.2 | 157.6 | 163
2 | 3 | 2030 | 54 | 56.1333 | 58.2667 | 60.4 | 62.5333 | 64.6667 | 67.4 | 70.1333 | 72.8667 | 75.6 | 78.3333 | 81.6 | 84.8667 | 88.1333 | 91.4 | 94.6667 | 98.6 | 102.5333 | 106.4667 | 110.4 | 114.3333 | 119.0667 | 123.8 | 128.5333 | 133.2667 | 138 | 143.6 | 149.2 | 154.8 | 160.4 | 166
3 | 0 | 3000 | 38.2222 | 39.7111 | 41.2 | 42.6889 | 44.1778 | 45.6667 | 47.4222 | 49.1778 | 50.9333 | 52.6889 | 54.4444 | 56.6889 | 58.9333 | 61.1778 | 63.4222 | 65.6667 | 68.0444 | 70.4222 | 72.8 | 75.1778 | 77.5556 | 80.6 | 83.6444 | 86.6889 | 89.7333 | 92.7778 | 96.1111 | 99.4444 | 102.7778 | 106.1111 | 109.4444
3 | 0.4 | 3004 | 38.2222 | 39.7111 | 41.2 | 42.6889 | 44.1778 | 45.6667 | 47.4222 | 49.1778 | 50.9333 | 52.6889 | 54.4444 | 56.6889 | 58.9333 | 61.1778 | 63.4222 | 65.6667 | 68.0444 | 70.4222 | 72.8 | 75.1778 | 77.5556 | 80.6 | 83.6444 | 86.6889 | 89.7333 | 92.7778 | 96.1111 | 99.4444 | 102.7778 | 106.1111 | 109.4444
3 | 0.6 | 3006 | 39.2222 | 40.8 | 42.3778 | 43.9556 | 45.5333 | 47.1111 | 48.9778 | 50.8444 | 52.7111 | 54.5778 | 56.4444 | 58.6 | 60.7556 | 62.9111 | 65.0667 | 67.2222 | 69.7778 | 72.3333 | 74.8889 | 77.4444 | 80 | 83.1333 | 86.2667 | 89.4 | 92.5333 | 95.6667 | 99.4 | 103.1333 | 106.8667 | 110.6 | 114.3333
3 | 0.8 | 3008 | 40.2222 | 41.8 | 43.3778 | 44.9556 | 46.5333 | 48.1111 | 49.9778 | 51.8444 | 53.7111 | 55.5778 | 57.4444 | 59.6889 | 61.9333 | 64.1778 | 66.4222 | 68.6667 | 71.4222 | 74.1778 | 76.9333 | 79.6889 | 82.4444 | 85.7778 | 89.1111 | 92.4444 | 95.7778 | 99.1111 | 102.9333 | 106.7556 | 110.5778 | 114.4 | 118.2222
3 | 1 | 3010 | 41.2222 | 42.8889 | 44.5556 | 46.2222 | 47.8889 | 49.5556 | 51.4222 | 53.2889 | 55.1556 | 57.0222 | 58.8889 | 61.2444 | 63.6 | 65.9556 | 68.3111 | 70.6667 | 73.5111 | 76.3556 | 79.2 | 82.0444 | 84.8889 | 88.4222 | 91.9556 | 95.4889 | 99.0222 | 102.5556 | 106.5778 | 110.6 | 114.6222 | 118.6444 | 122.6667
3 | 1.2 | 3012 | 42.6667 | 44.1333 | 45.6 | 47.0667 | 48.5333 | 50 | 52.0667 | 54.1333 | 56.2 | 58.2667 | 60.3333 | 62.6889 | 65.0444 | 67.4 | 69.7556 | 72.1111 | 75.1556 | 78.2 | 81.2444 | 84.2889 | 87.3333 | 90.8667 | 94.4 | 97.9333 | 101.4667 | 105 | 109.2222 | 113.4444 | 117.6667 | 121.8889 | 126.1111
3 | 1.4 | 3014 | 43.1111 | 44.6889 | 46.2667 | 47.8444 | 49.4222 | 51 | 53.1556 | 55.3111 | 57.4667 | 59.6222 | 61.7778 | 64.2222 | 66.6667 | 69.1111 | 71.5556 | 74 | 77.1556 | 80.3111 | 83.4667 | 86.6222 | 89.7778 | 93.4 | 97.0222 | 100.6444 | 104.2667 | 107.8889 | 112.3111 | 116.7333 | 121.1556 | 125.5778 | 130
3 | 1.6 | 3016 | 43.6667 | 45.4222 | 47.1778 | 48.9333 | 50.6889 | 52.4444 | 54.5111 | 56.5778 | 58.6444 | 60.7111 | 62.7778 | 65.4222 | 68.0667 | 70.7111 | 73.3556 | 76 | 79.1333 | 82.2667 | 85.4 | 88.5333 | 91.6667 | 95.5111 | 99.3556 | 103.2 | 107.0444 | 110.8889 | 115.2889 | 119.6889 | 124.0889 | 128.4889 | 132.8889
3 | 1.8 | 3018 | 45.1111 | 46.7778 | 48.4444 | 50.1111 | 51.7778 | 53.4444 | 55.6 | 57.7556 | 59.9111 | 62.0667 | 64.2222 | 66.8667 | 69.5111 | 72.1556 | 74.8 | 77.4444 | 80.7778 | 84.1111 | 87.4444 | 90.7778 | 94.1111 | 98.0444 | 101.9778 | 105.9111 | 109.8444 | 113.7778 | 118.2889 | 122.8 | 127.3111 | 131.8222 | 136.3333
3 | 2 | 3020 | 46.1111 | 47.8667 | 49.6222 | 51.3778 | 53.1333 | 54.8889 | 57.0444 | 59.2 | 61.3556 | 63.5111 | 65.6667 | 68.4222 | 71.1778 | 73.9333 | 76.6889 | 79.4444 | 82.7778 | 86.1111 | 89.4444 | 92.7778 | 96.1111 | 100.1333 | 104.1556 | 108.1778 | 112.2 | 116.2222 | 120.9333 | 125.6444 | 130.3556 | 135.0667 | 139.7778
3 | 2.2 | 3022 | 46.5556 | 48.4222 | 50.2889 | 52.1556 | 54.0222 | 55.8889 | 58.1333 | 60.3778 | 62.6222 | 64.8667 | 67.1111 | 70.0444 | 72.9778 | 75.9111 | 78.8444 | 81.7778 | 85.1333 | 88.4889 | 91.8444 | 95.2 | 98.5556 | 102.5778 | 106.6 | 110.6222 | 114.6444 | 118.6667 | 123.3778 | 128.0889 | 132.8 | 137.5111 | 142.2222
3 | 2.4 | 3024 | 47.5556 | 49.4222 | 51.2889 | 53.1556 | 55.0222 | 56.8889 | 59.1333 | 61.3778 | 63.6222 | 65.8667 | 68.1111 | 71.0667 | 74.0222 | 76.9778 | 79.9333 | 82.8889 | 86.3111 | 89.7333 | 93.1556 | 96.5778 | 100 | 104.2222 | 108.4444 | 112.6667 | 116.8889 | 121.1111 | 126.0222 | 130.9333 | 135.8444 | 140.7556 | 145.6667
3 | 2.6 | 3026 | 48.5556 | 50.5111 | 52.4667 | 54.4222 | 56.3778 | 58.3333 | 60.5778 | 62.8222 | 65.0667 | 67.3111 | 69.5556 | 72.5111 | 75.4667 | 78.4222 | 81.3778 | 84.3333 | 87.9556 | 91.5778 | 95.2 | 98.8222 | 102.4444 | 106.6667 | 110.8889 | 115.1111 | 119.3333 | 123.5556 | 128.5556 | 133.5556 | 138.5556 | 143.5556 | 148.5556
3 | 2.8 | 3028 | 49 | 50.9556 | 52.9111 | 54.8667 | 56.8222 | 58.7778 | 61.2222 | 63.6667 | 66.1111 | 68.5556 | 71 | 73.9556 | 76.9111 | 79.8667 | 82.8222 | 85.7778 | 89.5111 | 93.2444 | 96.9778 | 100.7111 | 104.4444 | 108.7556 | 113.0667 | 117.3778 | 121.6889 | 126 | 131 | 136 | 141 | 146 | 151
3 | 3 | 3030 | 50 | 51.9556 | 53.9111 | 55.8667 | 57.8222 | 59.7778 | 62.3333 | 64.8889 | 67.4444 | 70 | 72.5556 | 75.6 | 78.6444 | 81.6889 | 84.7333 | 87.7778 | 91.4 | 95.0222 | 98.6444 | 102.2667 | 105.8889 | 110.3111 | 114.7333 | 119.1556 | 123.5778 | 128 | 133.2 | 138.4 | 143.6 | 148.8 | 154
4 | 0 | 4000 | 35.1111 | 36.5556 | 38 | 39.4444 | 40.8889 | 42.3333 | 43.9111 | 45.4889 | 47.0667 | 48.6444 | 50.2222 | 52.2444 | 54.2667 | 56.2889 | 58.3111 | 60.3333 | 62.6222 | 64.9111 | 67.2 | 69.4889 | 71.7778 | 74.6 | 77.4222 | 80.2444 | 83.0667 | 85.8889 | 88.9556 | 92.0222 | 95.0889 | 98.1556 | 101.2222
4 | 0.4 | 4004 | 35.1111 | 36.5556 | 38 | 39.4444 | 40.8889 | 42.3333 | 43.9111 | 45.4889 | 47.0667 | 48.6444 | 50.2222 | 52.2444 | 54.2667 | 56.2889 | 58.3111 | 60.3333 | 62.6222 | 64.9111 | 67.2 | 69.4889 | 71.7778 | 74.6 | 77.4222 | 80.2444 | 83.0667 | 85.8889 | 88.9556 | 92.0222 | 95.0889 | 98.1556 | 101.2222
4 | 0.6 | 4006 | 36.1111 | 37.6 | 39.0889 | 40.5778 | 42.0667 | 43.5556 | 45.2889 | 47.0222 | 48.7556 | 50.4889 | 52.2222 | 54.2 | 56.1778 | 58.1556 | 60.1333 | 62.1111 | 64.4889 | 66.8667 | 69.2444 | 71.6222 | 74 | 76.8667 | 79.7333 | 82.6 | 85.4667 | 88.3333 | 91.8 | 95.2667 | 98.7333 | 102.2 | 105.6667
4 | 0.8 | 4008 | 37.1111 | 38.6 | 40.0889 | 41.5778 | 43.0667 | 44.5556 | 46.2889 | 48.0222 | 49.7556 | 51.4889 | 53.2222 | 55.2444 | 57.2667 | 59.2889 | 61.3111 | 63.3333 | 65.9111 | 68.4889 | 71.0667 | 73.6444 | 76.2222 | 79.2889 | 82.3556 | 85.4222 | 88.4889 | 91.5556 | 95.0667 | 98.5778 | 102.0889 | 105.6 | 109.1111
4 | 1 | 4010 | 38.1111 | 39.6444 | 41.1778 | 42.7111 | 44.2444 | 45.7778 | 47.5111 | 49.2444 | 50.9778 | 52.7111 | 54.4444 | 56.6222 | 58.8 | 60.9778 | 63.1556 | 65.3333 | 67.9556 | 70.5778 | 73.2 | 75.8222 | 78.4444 | 81.7111 | 84.9778 | 88.2444 | 91.5111 | 94.7778 | 98.4889 | 102.2 | 105.9111 | 109.6222 | 113.3333
4 | 1.2 | 4012 | 39.3333 | 40.6667 | 42 | 43.3333 | 44.6667 | 46 | 47.9333 | 49.8667 | 51.8 | 53.7333 | 55.6667 | 57.8444 | 60.0222 | 62.2 | 64.3778 | 66.5556 | 69.3778 | 72.2 | 75.0222 | 77.8444 | 80.6667 | 83.9333 | 87.2 | 90.4667 | 93.7333 | 97 | 100.9111 | 104.8222 | 108.7333 | 112.6444 | 116.5556
4 | 1.4 | 4014 | 39.5556 | 41.0444 | 42.5333 | 44.0222 | 45.5111 | 47 | 48.9778 | 50.9556 | 52.9333 | 54.9111 | 56.8889 | 59.1111 | 61.3333 | 63.5556 | 65.7778 | 68 | 70.9778 | 73.9556 | 76.9333 | 79.9111 | 82.8889 | 86.2 | 89.5111 | 92.8222 | 96.1333 | 99.4444 | 103.5556 | 107.6667 | 111.7778 | 115.8889 | 120
4 | 1.6 | 4016 | 40.3333 | 41.9111 | 43.4889 | 45.0667 | 46.6444 | 48.2222 | 50.1556 | 52.0889 | 54.0222 | 55.9556 | 57.8889 | 60.3111 | 62.7333 | 65.1556 | 67.5778 | 70 | 72.8667 | 75.7333 | 78.6 | 81.4667 | 84.3333 | 87.9556 | 91.5778 | 95.2 | 98.8222 | 102.4444 | 106.4444 | 110.4444 | 114.4444 | 118.4444 | 122.4444
4 | 1.8 | 4018 | 41.5556 | 43.0889 | 44.6222 | 46.1556 | 47.6889 | 49.2222 | 51.2 | 53.1778 | 55.1556 | 57.1333 | 59.1111 | 61.5333 | 63.9556 | 66.3778 | 68.8 | 71.2222 | 74.2889 | 77.3556 | 80.4222 | 83.4889 | 86.5556 | 90.2222 | 93.8889 | 97.5556 | 101.2222 | 104.8889 | 109.0444 | 113.2 | 117.3556 | 121.5111 | 125.6667
4 | 2 | 4020 | 42.5556 | 44.1333 | 45.7111 | 47.2889 | 48.8667 | 50.4444 | 52.4222 | 54.4 | 56.3778 | 58.3556 | 60.3333 | 62.9111 | 65.4889 | 68.0667 | 70.6444 | 73.2222 | 76.2889 | 79.3556 | 82.4222 | 85.4889 | 88.5556 | 92.2667 | 95.9778 | 99.6889 | 103.4 | 107.1111 | 111.4667 | 115.8222 | 120.1778 | 124.5333 | 128.8889
4 | 2.2 | 4022 | 42.7778 | 44.5111 | 46.2444 | 47.9778 | 49.7111 | 51.4444 | 53.4667 | 55.4889 | 57.5111 | 59.5333 | 61.5556 | 64.2222 | 66.8889 | 69.5556 | 72.2222 | 74.8889 | 78.0667 | 81.2444 | 84.4222 | 87.6 | 90.7778 | 94.4889 | 98.2 | 101.9111 | 105.6222 | 109.3333 | 113.6889 | 118.0444 | 122.4 | 126.7556 | 131.1111
4 | 2.4 | 4024 | 43.7778 | 45.5111 | 47.2444 | 48.9778 | 50.7111 | 52.4444 | 54.4667 | 56.4889 | 58.5111 | 60.5333 | 62.5556 | 65.3333 | 68.1111 | 70.8889 | 73.6667 | 76.4444 | 79.5556 | 82.6667 | 85.7778 | 88.8889 | 92 | 95.9111 | 99.8222 | 103.7333 | 107.6444 | 111.5556 | 116.1111 | 120.6667 | 125.2222 | 129.7778 | 134.3333
4 | 2.6 | 4026 | 44.7778 | 46.5556 | 48.3333 | 50.1111 | 51.8889 | 53.6667 | 55.6889 | 57.7111 | 59.7333 | 61.7556 | 63.7778 | 66.5556 | 69.3333 | 72.1111 | 74.8889 | 77.6667 | 80.9778 | 84.2889 | 87.6 | 90.9111 | 94.2222 | 98.1333 | 102.0444 | 105.9556 | 109.8667 | 113.7778 | 118.3778 | 122.9778 | 127.5778 | 132.1778 | 136.7778
4 | 2.8 | 4028 | 45 | 46.7778 | 48.5556 | 50.3333 | 52.1111 | 53.8889 | 56.1111 | 58.3333 | 60.5556 | 62.7778 | 65 | 67.7778 | 70.5556 | 73.3333 | 76.1111 | 78.8889 | 82.3556 | 85.8222 | 89.2889 | 92.7556 | 96.2222 | 100.1778 | 104.1333 | 108.0889 | 112.0444 | 116 | 120.6 | 125.2 | 129.8 | 134.4 | 139
4 | 3 | 4030 | 46 | 47.7778 | 49.5556 | 51.3333 | 53.1111 | 54.8889 | 57.2667 | 59.6444 | 62.0222 | 64.4 | 66.7778 | 69.6 | 72.4222 | 75.2444 | 78.0667 | 80.8889 | 84.2 | 87.5111 | 90.8222 | 94.1333 | 97.4444 | 101.5556 | 105.6667 | 109.7778 | 113.8889 | 118 | 122.8 | 127.6 | 132.4 | 137.2 | 142
5 | 0 | 5000 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 81.8 | 84.6 | 87.4 | 90.2 | 93
5 | 0.4 | 5004 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 81.8 | 84.6 | 87.4 | 90.2 | 93
5 | 0.6 | 5006 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.6 | 73.2 | 75.8 | 78.4 | 81 | 84.2 | 87.4 | 90.6 | 93.8 | 97
5 | 0.8 | 5008 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 50.8 | 52.6 | 54.4 | 56.2 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.2 | 90.4 | 93.6 | 96.8 | 100
5 | 1 | 5010 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 52 | 54 | 56 | 58 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 75 | 78 | 81 | 84 | 87 | 90.4 | 93.8 | 97.2 | 100.6 | 104
5 | 1.2 | 5012 | 36 | 37.2 | 38.4 | 39.6 | 40.8 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53 | 55 | 57 | 59 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.6 | 96.2 | 99.8 | 103.4 | 107
5 | 1.4 | 5014 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54 | 56 | 58 | 60 | 62 | 64.8 | 67.6 | 70.4 | 73.2 | 76 | 79 | 82 | 85 | 88 | 91 | 94.8 | 98.6 | 102.4 | 106.2 | 110
5 | 1.6 | 5016 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 80.4 | 83.8 | 87.2 | 90.6 | 94 | 97.6 | 101.2 | 104.8 | 108.4 | 112
5 | 1.8 | 5018 | 38 | 39.4 | 40.8 | 42.2 | 43.6 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 82.4 | 85.8 | 89.2 | 92.6 | 96 | 99.8 | 103.6 | 107.4 | 111.2 | 115
5 | 2 | 5020 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.4 | 87.8 | 91.2 | 94.6 | 98 | 102 | 106 | 110 | 114 | 118
5 | 2.2 | 5022 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56 | 58.4 | 60.8 | 63.2 | 65.6 | 68 | 71 | 74 | 77 | 80 | 83 | 86.4 | 89.8 | 93.2 | 96.6 | 100 | 104 | 108 | 112 | 116 | 120
5 | 2.4 | 5024 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.6 | 62.2 | 64.8 | 67.4 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.6 | 91.2 | 94.8 | 98.4 | 102 | 106.2 | 110.4 | 114.6 | 118.8 | 123
5 | 2.6 | 5026 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 50.8 | 52.6 | 54.4 | 56.2 | 58 | 60.6 | 63.2 | 65.8 | 68.4 | 71 | 74 | 77 | 80 | 83 | 86 | 89.6 | 93.2 | 96.8 | 100.4 | 104 | 108.2 | 112.4 | 116.6 | 120.8 | 125
5 | 2.8 | 5028 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51 | 53 | 55 | 57 | 59 | 61.6 | 64.2 | 66.8 | 69.4 | 72 | 75.2 | 78.4 | 81.6 | 84.8 | 88 | 91.6 | 95.2 | 98.8 | 102.4 | 106 | 110.2 | 114.4 | 118.6 | 122.8 | 127
5 | 3 | 5030 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 52.2 | 54.4 | 56.6 | 58.8 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.8 | 96.6 | 100.4 | 104.2 | 108 | 112.4 | 116.8 | 121.2 | 125.6 | 130
6 | 0 | 6000 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.52 | 47.24 | 48.96 | 50.68 | 52.4 | 54.48 | 56.56 | 58.64 | 60.72 | 62.8 | 65.24 | 67.68 | 70.12 | 72.56 | 75 | 77.68 | 80.36 | 83.04 | 85.72 | 88.4
6 | 0.4 | 6004 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.52 | 47.24 | 48.96 | 50.68 | 52.4 | 54.48 | 56.56 | 58.64 | 60.72 | 62.8 | 65.24 | 67.68 | 70.12 | 72.56 | 75 | 77.68 | 80.36 | 83.04 | 85.72 | 88.4
6 | 0.6 | 6006 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.32 | 49.04 | 50.76 | 52.48 | 54.2 | 56.28 | 58.36 | 60.44 | 62.52 | 64.6 | 67.08 | 69.56 | 72.04 | 74.52 | 77 | 80.04 | 83.08 | 86.12 | 89.16 | 92.2
6 | 0.8 | 6008 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.32 | 50.04 | 51.76 | 53.48 | 55.2 | 57.48 | 59.76 | 62.04 | 64.32 | 66.6 | 69.24 | 71.88 | 74.52 | 77.16 | 79.8 | 82.84 | 85.88 | 88.92 | 91.96 | 95
6 | 1 | 6010 | 33.2 | 34.52 | 35.84 | 37.16 | 38.48 | 39.8 | 41.32 | 42.84 | 44.36 | 45.88 | 47.4 | 49.32 | 51.24 | 53.16 | 55.08 | 57 | 59.28 | 61.56 | 63.84 | 66.12 | 68.4 | 71.24 | 74.08 | 76.92 | 79.76 | 82.6 | 85.84 | 89.08 | 92.32 | 95.56 | 98.8
6 | 1.2 | 6012 | 34.2 | 35.36 | 36.52 | 37.68 | 38.84 | 40 | 41.68 | 43.36 | 45.04 | 46.72 | 48.4 | 50.32 | 52.24 | 54.16 | 56.08 | 58 | 60.44 | 62.88 | 65.32 | 67.76 | 70.2 | 73.08 | 75.96 | 78.84 | 81.72 | 84.6 | 88 | 91.4 | 94.8 | 98.2 | 101.6
6 | 1.4 | 6014 | 34.2 | 35.56 | 36.92 | 38.28 | 39.64 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4 | 51.32 | 53.24 | 55.16 | 57.08 | 59 | 61.64 | 64.28 | 66.92 | 69.56 | 72.2 | 75.08 | 77.96 | 80.84 | 83.72 | 86.6 | 90.16 | 93.72 | 97.28 | 100.84 | 104.4
6 | 1.6 | 6016 | 35.2 | 36.52 | 37.84 | 39.16 | 40.48 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8 | 63.28 | 65.76 | 68.24 | 70.72 | 73.2 | 76.4 | 79.6 | 82.8 | 86 | 89.2 | 92.64 | 96.08 | 99.52 | 102.96 | 106.4
6 | 1.8 | 6018 | 36.2 | 37.52 | 38.84 | 40.16 | 41.48 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.48 | 55.56 | 57.64 | 59.72 | 61.8 | 64.48 | 67.16 | 69.84 | 72.52 | 75.2 | 78.4 | 81.6 | 84.8 | 88 | 91.2 | 94.8 | 98.4 | 102 | 105.6 | 109.2
6 | 2 | 6020 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.48 | 47.16 | 48.84 | 50.52 | 52.2 | 54.48 | 56.76 | 59.04 | 61.32 | 63.6 | 66.28 | 68.96 | 71.64 | 74.32 | 77 | 80.24 | 83.48 | 86.72 | 89.96 | 93.2 | 96.96 | 100.72 | 104.48 | 108.24 | 112
6 | 2.2 | 6022 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.48 | 57.76 | 60.04 | 62.32 | 64.6 | 67.44 | 70.28 | 73.12 | 75.96 | 78.8 | 82.04 | 85.28 | 88.52 | 91.76 | 95 | 98.8 | 102.6 | 106.4 | 110.2 | 114
6 | 2.4 | 6024 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.32 | 49.04 | 50.76 | 52.48 | 54.2 | 56.64 | 59.08 | 61.52 | 63.96 | 66.4 | 69.08 | 71.76 | 74.44 | 77.12 | 79.8 | 83.24 | 86.68 | 90.12 | 93.56 | 97 | 100.96 | 104.92 | 108.88 | 112.84 | 116.8
6 | 2.6 | 6026 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.32 | 50.04 | 51.76 | 53.48 | 55.2 | 57.64 | 60.08 | 62.52 | 64.96 | 67.4 | 70.28 | 73.16 | 76.04 | 78.92 | 81.8 | 85.2 | 88.6 | 92 | 95.4 | 98.8 | 102.8 | 106.8 | 110.8 | 114.8 | 118.8
6 | 2.8 | 6028 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.52 | 50.44 | 52.36 | 54.28 | 56.2 | 58.64 | 61.08 | 63.52 | 65.96 | 68.4 | 71.44 | 74.48 | 77.52 | 80.56 | 83.6 | 87.04 | 90.48 | 93.92 | 97.36 | 100.8 | 104.8 | 108.8 | 112.8 | 116.8 | 120.8
6 | 3 | 6030 | 40 | 41.52 | 43.04 | 44.56 | 46.08 | 47.6 | 49.68 | 51.76 | 53.84 | 55.92 | 58 | 60.44 | 62.88 | 65.32 | 67.76 | 70.2 | 73.08 | 75.96 | 78.84 | 81.72 | 84.6 | 88.2 | 91.8 | 95.4 | 99 | 102.6 | 106.76 | 110.92 | 115.08 | 119.24 | 123.4
7 | 0 | 7000 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.24 | 44.88 | 46.52 | 48.16 | 49.8 | 51.76 | 53.72 | 55.68 | 57.64 | 59.6 | 61.88 | 64.16 | 66.44 | 68.72 | 71 | 73.56 | 76.12 | 78.68 | 81.24 | 83.8
7 | 0.4 | 7004 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.24 | 44.88 | 46.52 | 48.16 | 49.8 | 51.76 | 53.72 | 55.68 | 57.64 | 59.6 | 61.88 | 64.16 | 66.44 | 68.72 | 71 | 73.56 | 76.12 | 78.68 | 81.24 | 83.8
7 | 0.6 | 7006 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.84 | 46.48 | 48.12 | 49.76 | 51.4 | 53.36 | 55.32 | 57.28 | 59.24 | 61.2 | 63.56 | 65.92 | 68.28 | 70.64 | 73 | 75.88 | 78.76 | 81.64 | 84.52 | 87.4
7 | 0.8 | 7008 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.84 | 47.48 | 49.12 | 50.76 | 52.4 | 54.56 | 56.72 | 58.88 | 61.04 | 63.2 | 65.68 | 68.16 | 70.64 | 73.12 | 75.6 | 78.48 | 81.36 | 84.24 | 87.12 | 90
7 | 1 | 7010 | 31.4 | 32.64 | 33.88 | 35.12 | 36.36 | 37.6 | 39.04 | 40.48 | 41.92 | 43.36 | 44.8 | 46.64 | 48.48 | 50.32 | 52.16 | 54 | 56.16 | 58.32 | 60.48 | 62.64 | 64.8 | 67.48 | 70.16 | 72.84 | 75.52 | 78.2 | 81.28 | 84.36 | 87.44 | 90.52 | 93.6
7 | 1.2 | 7012 | 32.4 | 33.52 | 34.64 | 35.76 | 36.88 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.64 | 49.48 | 51.32 | 53.16 | 55 | 57.28 | 59.56 | 61.84 | 64.12 | 66.4 | 69.16 | 71.92 | 74.68 | 77.44 | 80.2 | 83.4 | 86.6 | 89.8 | 93 | 96.2
7 | 1.4 | 7014 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.64 | 50.48 | 52.32 | 54.16 | 56 | 58.48 | 60.96 | 63.44 | 65.92 | 68.4 | 71.16 | 73.92 | 76.68 | 79.44 | 82.2 | 85.52 | 88.84 | 92.16 | 95.48 | 98.8
7 | 1.6 | 7016 | 33.4 | 34.64 | 35.88 | 37.12 | 38.36 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6 | 59.96 | 62.32 | 64.68 | 67.04 | 69.4 | 72.4 | 75.4 | 78.4 | 81.4 | 84.4 | 87.68 | 90.96 | 94.24 | 97.52 | 100.8
7 | 1.8 | 7018 | 34.4 | 35.64 | 36.88 | 38.12 | 39.36 | 40.6 | 42.24 | 43.88 | 45.52 | 47.16 | 48.8 | 50.76 | 52.72 | 54.68 | 56.64 | 58.6 | 61.16 | 63.72 | 66.28 | 68.84 | 71.4 | 74.4 | 77.4 | 80.4 | 83.4 | 86.4 | 89.8 | 93.2 | 96.6 | 100 | 103.4
7 | 2 | 7020 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.16 | 44.72 | 46.28 | 47.84 | 49.4 | 51.56 | 53.72 | 55.88 | 58.04 | 60.2 | 62.76 | 65.32 | 67.88 | 70.44 | 73 | 76.08 | 79.16 | 82.24 | 85.32 | 88.4 | 91.92 | 95.44 | 98.96 | 102.48 | 106
7 | 2.2 | 7022 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4 | 52.56 | 54.72 | 56.88 | 59.04 | 61.2 | 63.88 | 66.56 | 69.24 | 71.92 | 74.6 | 77.68 | 80.76 | 83.84 | 86.92 | 90 | 93.6 | 97.2 | 100.8 | 104.4 | 108
7 | 2.4 | 7024 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.84 | 46.48 | 48.12 | 49.76 | 51.4 | 53.68 | 55.96 | 58.24 | 60.52 | 62.8 | 65.36 | 67.92 | 70.48 | 73.04 | 75.6 | 78.88 | 82.16 | 85.44 | 88.72 | 92 | 95.72 | 99.44 | 103.16 | 106.88 | 110.6
7 | 2.6 | 7026 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.84 | 47.48 | 49.12 | 50.76 | 52.4 | 54.68 | 56.96 | 59.24 | 61.52 | 63.8 | 66.56 | 69.32 | 72.08 | 74.84 | 77.6 | 80.8 | 84 | 87.2 | 90.4 | 93.6 | 97.4 | 101.2 | 105 | 108.8 | 112.6
7 | 2.8 | 7028 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 46.04 | 47.88 | 49.72 | 51.56 | 53.4 | 55.68 | 57.96 | 60.24 | 62.52 | 64.8 | 67.68 | 70.56 | 73.44 | 76.32 | 79.2 | 82.48 | 85.76 | 89.04 | 92.32 | 95.6 | 99.4 | 103.2 | 107 | 110.8 | 114.6
7 | 3 | 7030 | 38 | 39.44 | 40.88 | 42.32 | 43.76 | 45.2 | 47.16 | 49.12 | 51.08 | 53.04 | 55 | 57.28 | 59.56 | 61.84 | 64.12 | 66.4 | 69.16 | 71.92 | 74.68 | 77.44 | 80.2 | 83.6 | 87 | 90.4 | 93.8 | 97.2 | 101.12 | 105.04 | 108.96 | 112.88 | 116.8
8 | 0 | 8000 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.96 | 42.52 | 44.08 | 45.64 | 47.2 | 49.04 | 50.88 | 52.72 | 54.56 | 56.4 | 58.52 | 60.64 | 62.76 | 64.88 | 67 | 69.44 | 71.88 | 74.32 | 76.76 | 79.2
8 | 0.4 | 8004 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.96 | 42.52 | 44.08 | 45.64 | 47.2 | 49.04 | 50.88 | 52.72 | 54.56 | 56.4 | 58.52 | 60.64 | 62.76 | 64.88 | 67 | 69.44 | 71.88 | 74.32 | 76.76 | 79.2
8 | 0.6 | 8006 | 28.2 | 29.36 | 30.52 | 31.68 | 32.84 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.36 | 43.92 | 45.48 | 47.04 | 48.6 | 50.44 | 52.28 | 54.12 | 55.96 | 57.8 | 60.04 | 62.28 | 64.52 | 66.76 | 69 | 71.72 | 74.44 | 77.16 | 79.88 | 82.6
8 | 0.8 | 8008 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.36 | 44.92 | 46.48 | 48.04 | 49.6 | 51.64 | 53.68 | 55.72 | 57.76 | 59.8 | 62.12 | 64.44 | 66.76 | 69.08 | 71.4 | 74.12 | 76.84 | 79.56 | 82.28 | 85
8 | 1 | 8010 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2 | 43.96 | 45.72 | 47.48 | 49.24 | 51 | 53.04 | 55.08 | 57.12 | 59.16 | 61.2 | 63.72 | 66.24 | 68.76 | 71.28 | 73.8 | 76.72 | 79.64 | 82.56 | 85.48 | 88.4
8 | 1.2 | 8012 | 30.6 | 31.68 | 32.76 | 33.84 | 34.92 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52 | 54.12 | 56.24 | 58.36 | 60.48 | 62.6 | 65.24 | 67.88 | 70.52 | 73.16 | 75.8 | 78.8 | 81.8 | 84.8 | 87.8 | 90.8
8 | 1.4 | 8014 | 30.6 | 31.88 | 33.16 | 34.44 | 35.72 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53 | 55.32 | 57.64 | 59.96 | 62.28 | 64.6 | 67.24 | 69.88 | 72.52 | 75.16 | 77.8 | 80.88 | 83.96 | 87.04 | 90.12 | 93.2
8 | 1.6 | 8016 | 31.6 | 32.76 | 33.92 | 35.08 | 36.24 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.04 | 48.88 | 50.72 | 52.56 | 54.4 | 56.64 | 58.88 | 61.12 | 63.36 | 65.6 | 68.4 | 71.2 | 74 | 76.8 | 79.6 | 82.72 | 85.84 | 88.96 | 92.08 | 95.2
8 | 1.8 | 8018 | 32.6 | 33.76 | 34.92 | 36.08 | 37.24 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.04 | 49.88 | 51.72 | 53.56 | 55.4 | 57.84 | 60.28 | 62.72 | 65.16 | 67.6 | 70.4 | 73.2 | 76 | 78.8 | 81.6 | 84.8 | 88 | 91.2 | 94.4 | 97.6
8 | 2 | 8020 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.84 | 42.28 | 43.72 | 45.16 | 46.6 | 48.64 | 50.68 | 52.72 | 54.76 | 56.8 | 59.24 | 61.68 | 64.12 | 66.56 | 69 | 71.92 | 74.84 | 77.76 | 80.68 | 83.6 | 86.88 | 90.16 | 93.44 | 96.72 | 100
8 | 2.2 | 8022 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.36 | 42.92 | 44.48 | 46.04 | 47.6 | 49.64 | 51.68 | 53.72 | 55.76 | 57.8 | 60.32 | 62.84 | 65.36 | 67.88 | 70.4 | 73.32 | 76.24 | 79.16 | 82.08 | 85 | 88.4 | 91.8 | 95.2 | 98.6 | 102
8 | 2.4 | 8024 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.36 | 43.92 | 45.48 | 47.04 | 48.6 | 50.72 | 52.84 | 54.96 | 57.08 | 59.2 | 61.64 | 64.08 | 66.52 | 68.96 | 71.4 | 74.52 | 77.64 | 80.76 | 83.88 | 87 | 90.48 | 93.96 | 97.44 | 100.92 | 104.4
8 | 2.6 | 8026 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.36 | 44.92 | 46.48 | 48.04 | 49.6 | 51.72 | 53.84 | 55.96 | 58.08 | 60.2 | 62.84 | 65.48 | 68.12 | 70.76 | 73.4 | 76.4 | 79.4 | 82.4 | 85.4 | 88.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4
8 | 2.8 | 8028 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.56 | 45.32 | 47.08 | 48.84 | 50.6 | 52.72 | 54.84 | 56.96 | 59.08 | 61.2 | 63.92 | 66.64 | 69.36 | 72.08 | 74.8 | 77.92 | 81.04 | 84.16 | 87.28 | 90.4 | 94 | 97.6 | 101.2 | 104.8 | 108.4
8 | 3 | 8030 | 36 | 37.36 | 38.72 | 40.08 | 41.44 | 42.8 | 44.64 | 46.48 | 48.32 | 50.16 | 52 | 54.12 | 56.24 | 58.36 | 60.48 | 62.6 | 65.24 | 67.88 | 70.52 | 73.16 | 75.8 | 79 | 82.2 | 85.4 | 88.6 | 91.8 | 95.48 | 99.16 | 102.84 | 106.52 | 110.2
9 | 0 | 9000 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.16 | 57.12 | 59.08 | 61.04 | 63 | 65.32 | 67.64 | 69.96 | 72.28 | 74.6
9 | 0.4 | 9004 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.16 | 57.12 | 59.08 | 61.04 | 63 | 65.32 | 67.64 | 69.96 | 72.28 | 74.6
9 | 0.6 | 9006 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.88 | 41.36 | 42.84 | 44.32 | 45.8 | 47.52 | 49.24 | 50.96 | 52.68 | 54.4 | 56.52 | 58.64 | 60.76 | 62.88 | 65 | 67.56 | 70.12 | 72.68 | 75.24 | 77.8
9 | 0.8 | 9008 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.88 | 42.36 | 43.84 | 45.32 | 46.8 | 48.72 | 50.64 | 52.56 | 54.48 | 56.4 | 58.56 | 60.72 | 62.88 | 65.04 | 67.2 | 69.76 | 72.32 | 74.88 | 77.44 | 80
9 | 1 | 9010 | 27.8 | 28.88 | 29.96 | 31.04 | 32.12 | 33.2 | 34.48 | 35.76 | 37.04 | 38.32 | 39.6 | 41.28 | 42.96 | 44.64 | 46.32 | 48 | 49.92 | 51.84 | 53.76 | 55.68 | 57.6 | 59.96 | 62.32 | 64.68 | 67.04 | 69.4 | 72.16 | 74.92 | 77.68 | 80.44 | 83.2
9 | 1.2 | 9012 | 28.8 | 29.84 | 30.88 | 31.92 | 32.96 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.28 | 43.96 | 45.64 | 47.32 | 49 | 50.96 | 52.92 | 54.88 | 56.84 | 58.8 | 61.32 | 63.84 | 66.36 | 68.88 | 71.4 | 74.2 | 77 | 79.8 | 82.6 | 85.4
9 | 1.4 | 9014 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.28 | 44.96 | 46.64 | 48.32 | 50 | 52.16 | 54.32 | 56.48 | 58.64 | 60.8 | 63.32 | 65.84 | 68.36 | 70.88 | 73.4 | 76.24 | 79.08 | 81.92 | 84.76 | 87.6
9 | 1.6 | 9016 | 29.8 | 30.88 | 31.96 | 33.04 | 34.12 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.32 | 46.04 | 47.76 | 49.48 | 51.2 | 53.32 | 55.44 | 57.56 | 59.68 | 61.8 | 64.4 | 67 | 69.6 | 72.2 | 74.8 | 77.76 | 80.72 | 83.68 | 86.64 | 89.6
9 | 1.8 | 9018 | 30.8 | 31.88 | 32.96 | 34.04 | 35.12 | 36.2 | 37.68 | 39.16 | 40.64 | 42.12 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2 | 54.52 | 56.84 | 59.16 | 61.48 | 63.8 | 66.4 | 69 | 71.6 | 74.2 | 76.8 | 79.8 | 82.8 | 85.8 | 88.8 | 91.8
9 | 2 | 9020 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.52 | 39.84 | 41.16 | 42.48 | 43.8 | 45.72 | 47.64 | 49.56 | 51.48 | 53.4 | 55.72 | 58.04 | 60.36 | 62.68 | 65 | 67.76 | 70.52 | 73.28 | 76.04 | 78.8 | 81.84 | 84.88 | 87.92 | 90.96 | 94
9 | 2.2 | 9022 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8 | 46.72 | 48.64 | 50.56 | 52.48 | 54.4 | 56.76 | 59.12 | 61.48 | 63.84 | 66.2 | 68.96 | 71.72 | 74.48 | 77.24 | 80 | 83.2 | 86.4 | 89.6 | 92.8 | 96
9 | 2.4 | 9024 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.88 | 41.36 | 42.84 | 44.32 | 45.8 | 47.76 | 49.72 | 51.68 | 53.64 | 55.6 | 57.92 | 60.24 | 62.56 | 64.88 | 67.2 | 70.16 | 73.12 | 76.08 | 79.04 | 82 | 85.24 | 88.48 | 91.72 | 94.96 | 98.2
9 | 2.6 | 9026 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.88 | 42.36 | 43.84 | 45.32 | 46.8 | 48.76 | 50.72 | 52.68 | 54.64 | 56.6 | 59.12 | 61.64 | 64.16 | 66.68 | 69.2 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86.6 | 90 | 93.4 | 96.8 | 100.2
9 | 2.8 | 9028 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 41.08 | 42.76 | 44.44 | 46.12 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6 | 60.16 | 62.72 | 65.28 | 67.84 | 70.4 | 73.36 | 76.32 | 79.28 | 82.24 | 85.2 | 88.6 | 92 | 95.4 | 98.8 | 102.2
9 | 3 | 9030 | 34 | 35.28 | 36.56 | 37.84 | 39.12 | 40.4 | 42.12 | 43.84 | 45.56 | 47.28 | 49 | 50.96 | 52.92 | 54.88 | 56.84 | 58.8 | 61.32 | 63.84 | 66.36 | 68.88 | 71.4 | 74.4 | 77.4 | 80.4 | 83.4 | 86.4 | 89.84 | 93.28 | 96.72 | 100.16 | 103.6
10 | 0 | 10000 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70
10 | 0.4 | 10004 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70
10 | 0.6 | 10006 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.6 | 46.2 | 47.8 | 49.4 | 51 | 53 | 55 | 57 | 59 | 61 | 63.4 | 65.8 | 68.2 | 70.6 | 73
10 | 0.8 | 10008 | 26 | 27 | 28 | 29 | 30 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55 | 57 | 59 | 61 | 63 | 65.4 | 67.8 | 70.2 | 72.6 | 75
10 | 1 | 10010 | 26 | 27 | 28 | 29 | 30 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78
10 | 1.2 | 10012 | 27 | 28 | 29 | 30 | 31 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.6 | 72.2 | 74.8 | 77.4 | 80
10 | 1.4 | 10014 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 49 | 51 | 53 | 55 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.6 | 74.2 | 76.8 | 79.4 | 82
10 | 1.6 | 10016 | 28 | 29 | 30 | 31 | 32 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 50 | 52 | 54 | 56 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84
10 | 1.8 | 10018 | 29 | 30 | 31 | 32 | 33 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51.2 | 53.4 | 55.6 | 57.8 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86
10 | 2 | 10020 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.2 | 37.4 | 38.6 | 39.8 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 52.2 | 54.4 | 56.6 | 58.8 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 76.8 | 79.6 | 82.4 | 85.2 | 88
10 | 2.2 | 10022 | 30 | 31 | 32 | 33 | 34 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53.2 | 55.4 | 57.6 | 59.8 | 62 | 64.6 | 67.2 | 69.8 | 72.4 | 75 | 78 | 81 | 84 | 87 | 90
10 | 2.4 | 10024 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63 | 65.8 | 68.6 | 71.4 | 74.2 | 77 | 80 | 83 | 86 | 89 | 92
10 | 2.6 | 10026 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.4 | 57.8 | 60.2 | 62.6 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78 | 81.2 | 84.4 | 87.6 | 90.8 | 94
10 | 2.8 | 10028 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.4 | 58.8 | 61.2 | 63.6 | 66 | 68.8 | 71.6 | 74.4 | 77.2 | 80 | 83.2 | 86.4 | 89.6 | 92.8 | 96
10 | 3 | 10030 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.2 | 87.4 | 90.6 | 93.8 | 97
11 | 0 | 11000 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.28 | 29.36 | 30.44 | 31.52 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.68 | 42.16 | 43.64 | 45.12 | 46.6 | 48.28 | 49.96 | 51.64 | 53.32 | 55 | 57.08 | 59.16 | 61.24 | 63.32 | 65.4
11 | 0.4 | 11004 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.28 | 29.36 | 30.44 | 31.52 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.68 | 42.16 | 43.64 | 45.12 | 46.6 | 48.28 | 49.96 | 51.64 | 53.32 | 55 | 57.08 | 59.16 | 61.24 | 63.32 | 65.4
11 | 0.6 | 11006 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2 | 41.68 | 43.16 | 44.64 | 46.12 | 47.6 | 49.48 | 51.36 | 53.24 | 55.12 | 57 | 59.24 | 61.48 | 63.72 | 65.96 | 68.2
11 | 0.8 | 11008 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 29.92 | 31.04 | 32.16 | 33.28 | 34.4 | 35.72 | 37.04 | 38.36 | 39.68 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4 | 51.28 | 53.16 | 55.04 | 56.92 | 58.8 | 61.04 | 63.28 | 65.52 | 67.76 | 70
11 | 1 | 11010 | 24.4 | 25.32 | 26.24 | 27.16 | 28.08 | 29 | 30.12 | 31.24 | 32.36 | 33.48 | 34.6 | 36.08 | 37.56 | 39.04 | 40.52 | 42 | 43.68 | 45.36 | 47.04 | 48.72 | 50.4 | 52.44 | 54.48 | 56.52 | 58.56 | 60.6 | 63.04 | 65.48 | 67.92 | 70.36 | 72.8
11 | 1.2 | 11012 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.92 | 38.44 | 39.96 | 41.48 | 43 | 44.68 | 46.36 | 48.04 | 49.72 | 51.4 | 53.64 | 55.88 | 58.12 | 60.36 | 62.6 | 65 | 67.4 | 69.8 | 72.2 | 74.6
11 | 1.4 | 11014 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8 | 45.68 | 47.56 | 49.44 | 51.32 | 53.2 | 55.44 | 57.68 | 59.92 | 62.16 | 64.4 | 66.84 | 69.28 | 71.72 | 74.16 | 76.6
11 | 1.6 | 11016 | 26.2 | 27.12 | 28.04 | 28.96 | 29.88 | 30.8 | 32.08 | 33.36 | 34.64 | 35.92 | 37.2 | 38.72 | 40.24 | 41.76 | 43.28 | 44.8 | 46.68 | 48.56 | 50.44 | 52.32 | 54.2 | 56.44 | 58.68 | 60.92 | 63.16 | 65.4 | 68 | 70.6 | 73.2 | 75.8 | 78.4
11 | 1.8 | 11018 | 27 | 27.96 | 28.92 | 29.88 | 30.84 | 31.8 | 33.08 | 34.36 | 35.64 | 36.92 | 38.2 | 39.72 | 41.24 | 42.76 | 44.28 | 45.8 | 47.84 | 49.88 | 51.92 | 53.96 | 56 | 58.24 | 60.48 | 62.72 | 64.96 | 67.2 | 69.84 | 72.48 | 75.12 | 77.76 | 80.4
11 | 2 | 11020 | 27 | 28.12 | 29.24 | 30.36 | 31.48 | 32.6 | 33.76 | 34.92 | 36.08 | 37.24 | 38.4 | 40.04 | 41.68 | 43.32 | 44.96 | 46.6 | 48.68 | 50.76 | 52.84 | 54.92 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.64 | 74.28 | 76.92 | 79.56 | 82.2
11 | 2.2 | 11022 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.88 | 42.56 | 44.24 | 45.92 | 47.6 | 49.64 | 51.68 | 53.72 | 55.76 | 57.8 | 60.24 | 62.68 | 65.12 | 67.56 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84
11 | 2.4 | 11024 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2 | 41.88 | 43.56 | 45.24 | 46.92 | 48.6 | 50.64 | 52.68 | 54.72 | 56.76 | 58.8 | 61.4 | 64 | 66.6 | 69.2 | 71.8 | 74.6 | 77.4 | 80.2 | 83 | 85.8
11 | 2.6 | 11026 | 28.8 | 29.92 | 31.04 | 32.16 | 33.28 | 34.4 | 35.72 | 37.04 | 38.36 | 39.68 | 41 | 42.72 | 44.44 | 46.16 | 47.88 | 49.6 | 51.8 | 54 | 56.2 | 58.4 | 60.6 | 63.04 | 65.48 | 67.92 | 70.36 | 72.8 | 75.8 | 78.8 | 81.8 | 84.8 | 87.8
11 | 2.8 | 11028 | 29 | 30.12 | 31.24 | 32.36 | 33.48 | 34.6 | 36.08 | 37.56 | 39.04 | 40.52 | 42 | 43.68 | 45.36 | 47.04 | 48.72 | 50.4 | 52.64 | 54.88 | 57.12 | 59.36 | 61.6 | 64.2 | 66.8 | 69.4 | 72 | 74.6 | 77.6 | 80.6 | 83.6 | 86.6 | 89.6
11 | 3 | 11030 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.88 | 38.36 | 39.84 | 41.32 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.64 | 55.88 | 58.12 | 60.36 | 62.6 | 65.2 | 67.8 | 70.4 | 73 | 75.6 | 78.6 | 81.6 | 84.6 | 87.6 | 90.6
12 | 0 | 12000 | 20.8 | 21.72 | 22.64 | 23.56 | 24.48 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.76 | 39.12 | 40.48 | 41.84 | 43.2 | 44.76 | 46.32 | 47.88 | 49.44 | 51 | 52.96 | 54.92 | 56.88 | 58.84 | 60.8
12 | 0.4 | 12004 | 20.8 | 21.72 | 22.64 | 23.56 | 24.48 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.76 | 39.12 | 40.48 | 41.84 | 43.2 | 44.76 | 46.32 | 47.88 | 49.44 | 51 | 52.96 | 54.92 | 56.88 | 58.84 | 60.8
12 | 0.6 | 12006 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 38.76 | 40.12 | 41.48 | 42.84 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53 | 55.08 | 57.16 | 59.24 | 61.32 | 63.4
12 | 0.8 | 12008 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 33.04 | 34.28 | 35.52 | 36.76 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.56 | 49.32 | 51.08 | 52.84 | 54.6 | 56.68 | 58.76 | 60.84 | 62.92 | 65
12 | 1 | 12010 | 22.8 | 23.64 | 24.48 | 25.32 | 26.16 | 27 | 28.04 | 29.08 | 30.12 | 31.16 | 32.2 | 33.56 | 34.92 | 36.28 | 37.64 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.68 | 50.56 | 52.44 | 54.32 | 56.2 | 58.48 | 60.76 | 63.04 | 65.32 | 67.6
12 | 1.2 | 12012 | 23.4 | 24.24 | 25.08 | 25.92 | 26.76 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8 | 34.24 | 35.68 | 37.12 | 38.56 | 40 | 41.56 | 43.12 | 44.68 | 46.24 | 47.8 | 49.88 | 51.96 | 54.04 | 56.12 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.2
12 | 1.4 | 12014 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.64 | 30.68 | 31.72 | 32.76 | 33.8 | 35.16 | 36.52 | 37.88 | 39.24 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.48 | 53.56 | 55.64 | 57.72 | 59.8 | 62.08 | 64.36 | 66.64 | 68.92 | 71.2
12 | 1.6 | 12016 | 24.4 | 25.24 | 26.08 | 26.92 | 27.76 | 28.6 | 29.76 | 30.92 | 32.08 | 33.24 | 34.4 | 35.84 | 37.28 | 38.72 | 40.16 | 41.6 | 43.36 | 45.12 | 46.88 | 48.64 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8 | 63.2 | 65.6 | 68 | 70.4 | 72.8
12 | 1.8 | 12018 | 25 | 25.92 | 26.84 | 27.76 | 28.68 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4 | 36.84 | 38.28 | 39.72 | 41.16 | 42.6 | 44.48 | 46.36 | 48.24 | 50.12 | 52 | 54.08 | 56.16 | 58.24 | 60.32 | 62.4 | 64.88 | 67.36 | 69.84 | 72.32 | 74.8
12 | 2 | 12020 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.32 | 32.44 | 33.56 | 34.68 | 35.8 | 37.28 | 38.76 | 40.24 | 41.72 | 43.2 | 45.16 | 47.12 | 49.08 | 51.04 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64 | 66.48 | 68.96 | 71.44 | 73.92 | 76.4
12 | 2.2 | 12022 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.08 | 47.96 | 49.84 | 51.72 | 53.6 | 55.88 | 58.16 | 60.44 | 62.72 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78
12 | 2.4 | 12024 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.08 | 48.96 | 50.84 | 52.72 | 54.6 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 79.6
12 | 2.6 | 12026 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 33.04 | 34.28 | 35.52 | 36.76 | 38 | 39.64 | 41.28 | 42.92 | 44.56 | 46.2 | 48.2 | 50.2 | 52.2 | 54.2 | 56.2 | 58.48 | 60.76 | 63.04 | 65.32 | 67.6 | 70.4 | 73.2 | 76 | 78.8 | 81.6
12 | 2.8 | 12028 | 27 | 28.04 | 29.08 | 30.12 | 31.16 | 32.2 | 33.56 | 34.92 | 36.28 | 37.64 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.88 | 50.96 | 53.04 | 55.12 | 57.2 | 59.6 | 62 | 64.4 | 66.8 | 69.2 | 72 | 74.8 | 77.6 | 80.4 | 83.2
12 | 3 | 12030 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8 | 34.16 | 35.52 | 36.88 | 38.24 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.88 | 51.96 | 54.04 | 56.12 | 58.2 | 60.6 | 63 | 65.4 | 67.8 | 70.2 | 73 | 75.8 | 78.6 | 81.4 | 84.2
13 | 0 | 13000 | 19.2 | 20.08 | 20.96 | 21.84 | 22.72 | 23.6 | 24.44 | 25.28 | 26.12 | 26.96 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.24 | 42.68 | 44.12 | 45.56 | 47 | 48.84 | 50.68 | 52.52 | 54.36 | 56.2
13 | 0.4 | 13004 | 19.2 | 20.08 | 20.96 | 21.84 | 22.72 | 23.6 | 24.44 | 25.28 | 26.12 | 26.96 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.24 | 42.68 | 44.12 | 45.56 | 47 | 48.84 | 50.68 | 52.52 | 54.36 | 56.2
13 | 0.6 | 13006 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6 | 35.84 | 37.08 | 38.32 | 39.56 | 40.8 | 42.44 | 44.08 | 45.72 | 47.36 | 49 | 50.92 | 52.84 | 54.76 | 56.68 | 58.6
13 | 0.8 | 13008 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.36 | 26.32 | 27.28 | 28.24 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.44 | 37.88 | 39.32 | 40.76 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4 | 52.32 | 54.24 | 56.16 | 58.08 | 60
13 | 1 | 13010 | 21.2 | 21.96 | 22.72 | 23.48 | 24.24 | 25 | 25.96 | 26.92 | 27.88 | 28.84 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.92 | 46.64 | 48.36 | 50.08 | 51.8 | 53.92 | 56.04 | 58.16 | 60.28 | 62.4
13 | 1.2 | 13012 | 21.6 | 22.36 | 23.12 | 23.88 | 24.64 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.56 | 32.92 | 34.28 | 35.64 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 46.12 | 48.04 | 49.96 | 51.88 | 53.8 | 55.8 | 57.8 | 59.8 | 61.8 | 63.8
13 | 1.4 | 13014 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.36 | 28.32 | 29.28 | 30.24 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 39.04 | 40.68 | 42.32 | 43.96 | 45.6 | 47.52 | 49.44 | 51.36 | 53.28 | 55.2 | 57.32 | 59.44 | 61.56 | 63.68 | 65.8
13 | 1.6 | 13016 | 22.6 | 23.36 | 24.12 | 24.88 | 25.64 | 26.4 | 27.44 | 28.48 | 29.52 | 30.56 | 31.6 | 32.96 | 34.32 | 35.68 | 37.04 | 38.4 | 40.04 | 41.68 | 43.32 | 44.96 | 46.6 | 48.52 | 50.44 | 52.36 | 54.28 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.2
13 | 1.8 | 13018 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.44 | 29.48 | 30.52 | 31.56 | 32.6 | 33.96 | 35.32 | 36.68 | 38.04 | 39.4 | 41.12 | 42.84 | 44.56 | 46.28 | 48 | 49.92 | 51.84 | 53.76 | 55.68 | 57.6 | 59.92 | 62.24 | 64.56 | 66.88 | 69.2
13 | 2 | 13020 | 23 | 23.96 | 24.92 | 25.88 | 26.84 | 27.8 | 28.88 | 29.96 | 31.04 | 32.12 | 33.2 | 34.52 | 35.84 | 37.16 | 38.48 | 39.8 | 41.64 | 43.48 | 45.32 | 47.16 | 49 | 51 | 53 | 55 | 57 | 59 | 61.32 | 63.64 | 65.96 | 68.28 | 70.6
13 | 2.2 | 13022 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 35.04 | 36.48 | 37.92 | 39.36 | 40.8 | 42.52 | 44.24 | 45.96 | 47.68 | 49.4 | 51.52 | 53.64 | 55.76 | 57.88 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72
13 | 2.4 | 13024 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6 | 36.04 | 37.48 | 38.92 | 40.36 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.6 | 54.8 | 57 | 59.2 | 61.4 | 63.8 | 66.2 | 68.6 | 71 | 73.4
13 | 2.6 | 13026 | 24.4 | 25.36 | 26.32 | 27.28 | 28.24 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.56 | 38.12 | 39.68 | 41.24 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 51.8 | 53.92 | 56.04 | 58.16 | 60.28 | 62.4 | 65 | 67.6 | 70.2 | 72.8 | 75.4
13 | 2.8 | 13028 | 25 | 25.96 | 26.92 | 27.88 | 28.84 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 45.12 | 47.04 | 48.96 | 50.88 | 52.8 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66.4 | 69 | 71.6 | 74.2 | 76.8
13 | 3 | 13030 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.12 | 48.04 | 49.96 | 51.88 | 53.8 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67.4 | 70 | 72.6 | 75.2 | 77.8
14 | 0 | 14000 | 17.6 | 18.44 | 19.28 | 20.12 | 20.96 | 21.8 | 22.52 | 23.24 | 23.96 | 24.68 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.72 | 39.04 | 40.36 | 41.68 | 43 | 44.72 | 46.44 | 48.16 | 49.88 | 51.6
14 | 0.4 | 14004 | 17.6 | 18.44 | 19.28 | 20.12 | 20.96 | 21.8 | 22.52 | 23.24 | 23.96 | 24.68 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.72 | 39.04 | 40.36 | 41.68 | 43 | 44.72 | 46.44 | 48.16 | 49.88 | 51.6
14 | 0.6 | 14006 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4 | 38.92 | 40.44 | 41.96 | 43.48 | 45 | 46.76 | 48.52 | 50.28 | 52.04 | 53.8
14 | 0.8 | 14008 | 18.8 | 19.48 | 20.16 | 20.84 | 21.52 | 22.2 | 23.08 | 23.96 | 24.84 | 25.72 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.32 | 34.64 | 35.96 | 37.28 | 38.6 | 40.12 | 41.64 | 43.16 | 44.68 | 46.2 | 47.96 | 49.72 | 51.48 | 53.24 | 55
14 | 1 | 14010 | 19.6 | 20.28 | 20.96 | 21.64 | 22.32 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.52 | 29.64 | 30.76 | 31.88 | 33 | 34.32 | 35.64 | 36.96 | 38.28 | 39.6 | 41.16 | 42.72 | 44.28 | 45.84 | 47.4 | 49.36 | 51.32 | 53.28 | 55.24 | 57.2
14 | 1.2 | 14012 | 19.8 | 20.48 | 21.16 | 21.84 | 22.52 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6 | 28.88 | 30.16 | 31.44 | 32.72 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.2 | 53 | 54.8 | 56.6 | 58.4
14 | 1.4 | 14014 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.08 | 25.96 | 26.84 | 27.72 | 28.6 | 29.72 | 30.84 | 31.96 | 33.08 | 34.2 | 35.72 | 37.24 | 38.76 | 40.28 | 41.8 | 43.56 | 45.32 | 47.08 | 48.84 | 50.6 | 52.56 | 54.52 | 56.48 | 58.44 | 60.4
14 | 1.6 | 14016 | 20.8 | 21.48 | 22.16 | 22.84 | 23.52 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 30.08 | 31.36 | 32.64 | 33.92 | 35.2 | 36.72 | 38.24 | 39.76 | 41.28 | 42.8 | 44.56 | 46.32 | 48.08 | 49.84 | 51.6 | 53.6 | 55.6 | 57.6 | 59.6 | 61.6
14 | 1.8 | 14018 | 21 | 21.84 | 22.68 | 23.52 | 24.36 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 31.08 | 32.36 | 33.64 | 34.92 | 36.2 | 37.76 | 39.32 | 40.88 | 42.44 | 44 | 45.76 | 47.52 | 49.28 | 51.04 | 52.8 | 54.96 | 57.12 | 59.28 | 61.44 | 63.6
14 | 2 | 14020 | 21 | 21.88 | 22.76 | 23.64 | 24.52 | 25.4 | 26.44 | 27.48 | 28.52 | 29.56 | 30.6 | 31.76 | 32.92 | 34.08 | 35.24 | 36.4 | 38.12 | 39.84 | 41.56 | 43.28 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.16 | 58.32 | 60.48 | 62.64 | 64.8
14 | 2.2 | 14022 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.16 | 49.12 | 51.08 | 53.04 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66
14 | 2.4 | 14024 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8 | 33.12 | 34.44 | 35.76 | 37.08 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.2 | 50.2 | 52.2 | 54.2 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.2
14 | 2.6 | 14026 | 22.2 | 23.08 | 23.96 | 24.84 | 25.72 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.48 | 34.96 | 36.44 | 37.92 | 39.4 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49.36 | 51.32 | 53.28 | 55.24 | 57.2 | 59.6 | 62 | 64.4 | 66.8 | 69.2
14 | 2.8 | 14028 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.52 | 29.64 | 30.76 | 31.88 | 33 | 34.32 | 35.64 | 36.96 | 38.28 | 39.6 | 41.36 | 43.12 | 44.88 | 46.64 | 48.4 | 50.4 | 52.4 | 54.4 | 56.4 | 58.4 | 60.8 | 63.2 | 65.6 | 68 | 70.4
14 | 3 | 14030 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.68 | 36.16 | 37.64 | 39.12 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.4 | 53.4 | 55.4 | 57.4 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.4
15 | 0 | 15000 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
15 | 0.4 | 15004 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
15 | 0.6 | 15006 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49
15 | 0.8 | 15008 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50
15 | 1 | 15010 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52
15 | 1.2 | 15012 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26.2 | 27.4 | 28.6 | 29.8 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.6 | 48.2 | 49.8 | 51.4 | 53
15 | 1.4 | 15014 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27 | 28 | 29 | 30 | 31 | 32.4 | 33.8 | 35.2 | 36.6 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55
15 | 1.6 | 15016 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56
15 | 1.8 | 15018 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 23.8 | 24.6 | 25.4 | 26.2 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 50 | 52 | 54 | 56 | 58
15 | 2 | 15020 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.6 | 36.2 | 37.8 | 39.4 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51 | 53 | 55 | 57 | 59
15 | 2.2 | 15022 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 52 | 54 | 56 | 58 | 60
15 | 2.4 | 15024 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53 | 55 | 57 | 59 | 61
15 | 2.6 | 15026 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.4 | 31.8 | 33.2 | 34.6 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63
15 | 2.8 | 15028 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.6 | 39.2 | 40.8 | 42.4 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64
15 | 3 | 15030 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.4 | 32.8 | 34.2 | 35.6 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65
16 | 0 | 16000 | 15.2 | 15.96 | 16.72 | 17.48 | 18.24 | 19 | 19.56 | 20.12 | 20.68 | 21.24 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.56 | 33.72 | 34.88 | 36.04 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6
16 | 0.4 | 16004 | 15.2 | 15.96 | 16.72 | 17.48 | 18.24 | 19 | 19.56 | 20.12 | 20.68 | 21.24 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.56 | 33.72 | 34.88 | 36.04 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6
16 | 0.6 | 16006 | 16.2 | 16.76 | 17.32 | 17.88 | 18.44 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.72 | 24.64 | 25.56 | 26.48 | 27.4 | 28.4 | 29.4 | 30.4 | 31.4 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.48 | 41.96 | 43.44 | 44.92 | 46.4
16 | 0.8 | 16008 | 16.2 | 16.76 | 17.32 | 17.88 | 18.44 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40 | 41.52 | 43.04 | 44.56 | 46.08 | 47.6
16 | 1 | 16010 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.72 | 25.64 | 26.56 | 27.48 | 28.4 | 29.56 | 30.72 | 31.88 | 33.04 | 34.2 | 35.56 | 36.92 | 38.28 | 39.64 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4
16 | 1.2 | 16012 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.92 | 26.04 | 27.16 | 28.28 | 29.4 | 30.56 | 31.72 | 32.88 | 34.04 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.16 | 45.72 | 47.28 | 48.84 | 50.4
16 | 1.4 | 16014 | 17.2 | 17.92 | 18.64 | 19.36 | 20.08 | 20.8 | 21.56 | 22.32 | 23.08 | 23.84 | 24.6 | 25.56 | 26.52 | 27.48 | 28.44 | 29.4 | 30.72 | 32.04 | 33.36 | 34.68 | 36 | 37.52 | 39.04 | 40.56 | 42.08 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2
16 | 1.6 | 16016 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.76 | 22.52 | 23.28 | 24.04 | 24.8 | 25.92 | 27.04 | 28.16 | 29.28 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.52 | 40.04 | 41.56 | 43.08 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2
16 | 1.8 | 16018 | 18 | 18.76 | 19.52 | 20.28 | 21.04 | 21.8 | 22.56 | 23.32 | 24.08 | 24.84 | 25.6 | 26.76 | 27.92 | 29.08 | 30.24 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.48 | 49.36 | 51.24 | 53.12 | 55
16 | 2 | 16020 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.88 | 34.36 | 35.84 | 37.32 | 38.8 | 40.36 | 41.92 | 43.48 | 45.04 | 46.6 | 48.48 | 50.36 | 52.24 | 54.12 | 56
16 | 2.2 | 16022 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 22.92 | 23.84 | 24.76 | 25.68 | 26.6 | 27.76 | 28.92 | 30.08 | 31.24 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.72 | 42.44 | 44.16 | 45.88 | 47.6 | 49.48 | 51.36 | 53.24 | 55.12 | 57
16 | 2.4 | 16024 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40 | 41.68 | 43.36 | 45.04 | 46.72 | 48.4 | 50.32 | 52.24 | 54.16 | 56.08 | 58
16 | 2.6 | 16026 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.92 | 30.24 | 31.56 | 32.88 | 34.2 | 35.52 | 36.84 | 38.16 | 39.48 | 40.8 | 42.52 | 44.24 | 45.96 | 47.68 | 49.4 | 51.48 | 53.56 | 55.64 | 57.72 | 59.8
16 | 2.8 | 16028 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.72 | 25.64 | 26.56 | 27.48 | 28.4 | 29.56 | 30.72 | 31.88 | 33.04 | 34.2 | 35.72 | 37.24 | 38.76 | 40.28 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8
16 | 3 | 16030 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.76 | 25.72 | 26.68 | 27.64 | 28.6 | 29.92 | 31.24 | 32.56 | 33.88 | 35.2 | 36.72 | 38.24 | 39.76 | 41.28 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.48 | 55.56 | 57.64 | 59.72 | 61.8
17 | 0 | 17000 | 14.4 | 15.12 | 15.84 | 16.56 | 17.28 | 18 | 18.52 | 19.04 | 19.56 | 20.08 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
17 | 0.4 | 17004 | 14.4 | 15.12 | 15.84 | 16.56 | 17.28 | 18 | 18.52 | 19.04 | 19.56 | 20.08 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
17 | 0.6 | 17006 | 15.4 | 15.92 | 16.44 | 16.96 | 17.48 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.44 | 23.28 | 24.12 | 24.96 | 25.8 | 26.8 | 27.8 | 28.8 | 29.8 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8
17 | 0.8 | 17008 | 15.4 | 15.92 | 16.44 | 16.96 | 17.48 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.24 | 28.28 | 29.32 | 30.36 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.44 | 40.88 | 42.32 | 43.76 | 45.2
17 | 1 | 17010 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.44 | 24.28 | 25.12 | 25.96 | 26.8 | 27.92 | 29.04 | 30.16 | 31.28 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8
17 | 1.2 | 17012 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.64 | 24.68 | 25.72 | 26.76 | 27.8 | 28.92 | 30.04 | 31.16 | 32.28 | 33.4 | 34.76 | 36.12 | 37.48 | 38.84 | 40.2 | 41.72 | 43.24 | 44.76 | 46.28 | 47.8
17 | 1.4 | 17014 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.32 | 21.04 | 21.76 | 22.48 | 23.2 | 24.12 | 25.04 | 25.96 | 26.88 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.44 | 36.88 | 38.32 | 39.76 | 41.2 | 42.84 | 44.48 | 46.12 | 47.76 | 49.4
17 | 1.6 | 17016 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.72 | 21.44 | 22.16 | 22.88 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.44 | 37.88 | 39.32 | 40.76 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4
17 | 1.8 | 17018 | 17 | 17.72 | 18.44 | 19.16 | 19.88 | 20.6 | 21.32 | 22.04 | 22.76 | 23.48 | 24.2 | 25.32 | 26.44 | 27.56 | 28.68 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52
17 | 2 | 17020 | 17.4 | 18.04 | 18.68 | 19.32 | 19.96 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 31.16 | 32.52 | 33.88 | 35.24 | 36.6 | 38.12 | 39.64 | 41.16 | 42.68 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53
17 | 2.2 | 17022 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.84 | 22.68 | 23.52 | 24.36 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.64 | 40.28 | 41.92 | 43.56 | 45.2 | 46.96 | 48.72 | 50.48 | 52.24 | 54
17 | 2.4 | 17024 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.24 | 28.28 | 29.32 | 30.36 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.64 | 49.48 | 51.32 | 53.16 | 55
17 | 2.6 | 17026 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.44 | 28.68 | 29.92 | 31.16 | 32.4 | 33.64 | 34.88 | 36.12 | 37.36 | 38.6 | 40.24 | 41.88 | 43.52 | 45.16 | 46.8 | 48.76 | 50.72 | 52.68 | 54.64 | 56.6
17 | 2.8 | 17028 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.44 | 24.28 | 25.12 | 25.96 | 26.8 | 27.92 | 29.04 | 30.16 | 31.28 | 32.4 | 33.84 | 35.28 | 36.72 | 38.16 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6
17 | 3 | 17030 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.52 | 24.44 | 25.36 | 26.28 | 27.2 | 28.44 | 29.68 | 30.92 | 32.16 | 33.4 | 34.84 | 36.28 | 37.72 | 39.16 | 40.6 | 42.24 | 43.88 | 45.52 | 47.16 | 48.8 | 50.76 | 52.72 | 54.68 | 56.64 | 58.6
18 | 0 | 18000 | 13.6 | 14.28 | 14.96 | 15.64 | 16.32 | 17 | 17.48 | 17.96 | 18.44 | 18.92 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.28 | 30.36 | 31.44 | 32.52 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8
18 | 0.4 | 18004 | 13.6 | 14.28 | 14.96 | 15.64 | 16.32 | 17 | 17.48 | 17.96 | 18.44 | 18.92 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.28 | 30.36 | 31.44 | 32.52 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8
18 | 0.6 | 18006 | 14.6 | 15.08 | 15.56 | 16.04 | 16.52 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.16 | 21.92 | 22.68 | 23.44 | 24.2 | 25.2 | 26.2 | 27.2 | 28.2 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.24 | 37.48 | 38.72 | 39.96 | 41.2
18 | 0.8 | 18008 | 14.6 | 15.08 | 15.56 | 16.04 | 16.52 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.76 | 26.72 | 27.68 | 28.64 | 29.6 | 30.88 | 32.16 | 33.44 | 34.72 | 36 | 37.36 | 38.72 | 40.08 | 41.44 | 42.8
18 | 1 | 18010 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.16 | 22.92 | 23.68 | 24.44 | 25.2 | 26.28 | 27.36 | 28.44 | 29.52 | 30.6 | 31.88 | 33.16 | 34.44 | 35.72 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2
18 | 1.2 | 18012 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.36 | 23.32 | 24.28 | 25.24 | 26.2 | 27.28 | 28.36 | 29.44 | 30.52 | 31.6 | 32.84 | 34.08 | 35.32 | 36.56 | 37.8 | 39.28 | 40.76 | 42.24 | 43.72 | 45.2
18 | 1.4 | 18014 | 15.6 | 16.16 | 16.72 | 17.28 | 17.84 | 18.4 | 19.08 | 19.76 | 20.44 | 21.12 | 21.8 | 22.68 | 23.56 | 24.44 | 25.32 | 26.2 | 27.36 | 28.52 | 29.68 | 30.84 | 32 | 33.36 | 34.72 | 36.08 | 37.44 | 38.8 | 40.36 | 41.92 | 43.48 | 45.04 | 46.6
18 | 1.6 | 18016 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.68 | 20.36 | 21.04 | 21.72 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.36 | 35.72 | 37.08 | 38.44 | 39.8 | 41.36 | 42.92 | 44.48 | 46.04 | 47.6
18 | 1.8 | 18018 | 16 | 16.68 | 17.36 | 18.04 | 18.72 | 19.4 | 20.08 | 20.76 | 21.44 | 22.12 | 22.8 | 23.88 | 24.96 | 26.04 | 27.12 | 28.2 | 29.36 | 30.52 | 31.68 | 32.84 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.44 | 44.08 | 45.72 | 47.36 | 49
18 | 2 | 18020 | 16.6 | 17.16 | 17.72 | 18.28 | 18.84 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.44 | 30.68 | 31.92 | 33.16 | 34.4 | 35.88 | 37.36 | 38.84 | 40.32 | 41.8 | 43.44 | 45.08 | 46.72 | 48.36 | 50
18 | 2.2 | 18022 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.88 | 25.96 | 27.04 | 28.12 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.56 | 38.12 | 39.68 | 41.24 | 42.8 | 44.44 | 46.08 | 47.72 | 49.36 | 51
18 | 2.4 | 18024 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.76 | 26.72 | 27.68 | 28.64 | 29.6 | 30.88 | 32.16 | 33.44 | 34.72 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52
18 | 2.6 | 18026 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.96 | 27.12 | 28.28 | 29.44 | 30.6 | 31.76 | 32.92 | 34.08 | 35.24 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.04 | 47.88 | 49.72 | 51.56 | 53.4
18 | 2.8 | 18028 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.16 | 22.92 | 23.68 | 24.44 | 25.2 | 26.28 | 27.36 | 28.44 | 29.52 | 30.6 | 31.96 | 33.32 | 34.68 | 36.04 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.04 | 48.88 | 50.72 | 52.56 | 54.4
18 | 3 | 18030 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.28 | 23.16 | 24.04 | 24.92 | 25.8 | 26.96 | 28.12 | 29.28 | 30.44 | 31.6 | 32.96 | 34.32 | 35.68 | 37.04 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.04 | 49.88 | 51.72 | 53.56 | 55.4
19 | 0 | 19000 | 12.8 | 13.44 | 14.08 | 14.72 | 15.36 | 16 | 16.44 | 16.88 | 17.32 | 17.76 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4
19 | 0.4 | 19004 | 12.8 | 13.44 | 14.08 | 14.72 | 15.36 | 16 | 16.44 | 16.88 | 17.32 | 17.76 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4
19 | 0.6 | 19006 | 13.8 | 14.24 | 14.68 | 15.12 | 15.56 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 19.88 | 20.56 | 21.24 | 21.92 | 22.6 | 23.6 | 24.6 | 25.6 | 26.6 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.12 | 35.24 | 36.36 | 37.48 | 38.6
19 | 0.8 | 19008 | 13.8 | 14.24 | 14.68 | 15.12 | 15.56 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.28 | 25.16 | 26.04 | 26.92 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.28 | 36.56 | 37.84 | 39.12 | 40.4
19 | 1 | 19010 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 20.88 | 21.56 | 22.24 | 22.92 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6
19 | 1.2 | 19012 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 21.08 | 21.96 | 22.84 | 23.72 | 24.6 | 25.64 | 26.68 | 27.72 | 28.76 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.84 | 38.28 | 39.72 | 41.16 | 42.6
19 | 1.4 | 19014 | 14.8 | 15.28 | 15.76 | 16.24 | 16.72 | 17.2 | 17.84 | 18.48 | 19.12 | 19.76 | 20.4 | 21.24 | 22.08 | 22.92 | 23.76 | 24.6 | 25.68 | 26.76 | 27.84 | 28.92 | 30 | 31.28 | 32.56 | 33.84 | 35.12 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8
19 | 1.6 | 19016 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.64 | 19.28 | 19.92 | 20.56 | 21.2 | 22.08 | 22.96 | 23.84 | 24.72 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.28 | 33.56 | 34.84 | 36.12 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8
19 | 1.8 | 19018 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.84 | 19.48 | 20.12 | 20.76 | 21.4 | 22.44 | 23.48 | 24.52 | 25.56 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.92 | 41.44 | 42.96 | 44.48 | 46
19 | 2 | 19020 | 15.8 | 16.28 | 16.76 | 17.24 | 17.72 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.72 | 28.84 | 29.96 | 31.08 | 32.2 | 33.64 | 35.08 | 36.52 | 37.96 | 39.4 | 40.92 | 42.44 | 43.96 | 45.48 | 47
19 | 2.2 | 19022 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.68 | 20.36 | 21.04 | 21.72 | 22.4 | 23.44 | 24.48 | 25.52 | 26.56 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.48 | 35.96 | 37.44 | 38.92 | 40.4 | 41.92 | 43.44 | 44.96 | 46.48 | 48
19 | 2.4 | 19024 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.28 | 25.16 | 26.04 | 26.92 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.28 | 43.96 | 45.64 | 47.32 | 49
19 | 2.6 | 19026 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.48 | 25.56 | 26.64 | 27.72 | 28.8 | 29.88 | 30.96 | 32.04 | 33.12 | 34.2 | 35.68 | 37.16 | 38.64 | 40.12 | 41.6 | 43.32 | 45.04 | 46.76 | 48.48 | 50.2
19 | 2.8 | 19028 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 20.88 | 21.56 | 22.24 | 22.92 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.08 | 31.36 | 32.64 | 33.92 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.32 | 46.04 | 47.76 | 49.48 | 51.2
19 | 3 | 19030 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 21.04 | 21.88 | 22.72 | 23.56 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 31.08 | 32.36 | 33.64 | 34.92 | 36.2 | 37.68 | 39.16 | 40.64 | 42.12 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2
20 | 0 | 20000 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
20 | 0.4 | 20004 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
20 | 0.6 | 20006 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36
20 | 0.8 | 20008 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38
20 | 1 | 20010 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 23 | 24 | 25 | 26 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39
20 | 1.2 | 20012 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40
20 | 1.4 | 20014 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41
20 | 1.6 | 20016 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42
20 | 1.8 | 20018 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43
20 | 2 | 20020 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.4 | 32.8 | 34.2 | 35.6 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44
20 | 2.2 | 20022 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32.4 | 33.8 | 35.2 | 36.6 | 38 | 39.4 | 40.8 | 42.2 | 43.6 | 45
20 | 2.4 | 20024 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46
20 | 2.6 | 20026 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
20 | 2.8 | 20028 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 23 | 24 | 25 | 26 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48
20 | 3 | 20030 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49
21 | 0 | 21000 | 11.2 | 11.76 | 12.32 | 12.88 | 13.44 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6
21 | 0.4 | 21004 | 11.2 | 11.76 | 12.32 | 12.88 | 13.44 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6
21 | 0.6 | 21006 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.36 | 17.92 | 18.48 | 19.04 | 19.6 | 20.52 | 21.44 | 22.36 | 23.28 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 29.76 | 30.72 | 31.68 | 32.64 | 33.6
21 | 0.8 | 21008 | 12.2 | 12.56 | 12.92 | 13.28 | 13.64 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4
21 | 1 | 21010 | 12.2 | 12.72 | 13.24 | 13.76 | 14.28 | 14.8 | 15.36 | 15.92 | 16.48 | 17.04 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4
21 | 1.2 | 21012 | 12.2 | 12.76 | 13.32 | 13.88 | 14.44 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.52 | 19.24 | 19.96 | 20.68 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 26.96 | 27.92 | 28.88 | 29.84 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4
21 | 1.4 | 21014 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.32 | 28.44 | 29.56 | 30.68 | 31.8 | 33.08 | 34.36 | 35.64 | 36.92 | 38.2
21 | 1.6 | 21016 | 13 | 13.56 | 14.12 | 14.68 | 15.24 | 15.8 | 16.36 | 16.92 | 17.48 | 18.04 | 18.6 | 19.36 | 20.12 | 20.88 | 21.64 | 22.4 | 23.32 | 24.24 | 25.16 | 26.08 | 27 | 28.12 | 29.24 | 30.36 | 31.48 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2
21 | 1.8 | 21018 | 13.2 | 13.72 | 14.24 | 14.76 | 15.28 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.68 | 20.56 | 21.44 | 22.32 | 23.2 | 24.16 | 25.12 | 26.08 | 27.04 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2
21 | 2 | 21020 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.32 | 30.64 | 31.96 | 33.28 | 34.6 | 35.88 | 37.16 | 38.44 | 39.72 | 41
21 | 2.2 | 21022 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.36 | 17.92 | 18.48 | 19.04 | 19.6 | 20.52 | 21.44 | 22.36 | 23.28 | 24.2 | 25.16 | 26.12 | 27.08 | 28.04 | 29 | 30.28 | 31.56 | 32.84 | 34.12 | 35.4 | 36.72 | 38.04 | 39.36 | 40.68 | 42
21 | 2.4 | 21024 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.52 | 18.24 | 18.96 | 19.68 | 20.4 | 21.16 | 21.92 | 22.68 | 23.44 | 24.2 | 25.32 | 26.44 | 27.56 | 28.68 | 29.8 | 30.96 | 32.12 | 33.28 | 34.44 | 35.6 | 37.08 | 38.56 | 40.04 | 41.52 | 43
21 | 2.6 | 21026 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.16 | 27.12 | 28.08 | 29.04 | 30 | 31.28 | 32.56 | 33.84 | 35.12 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8
21 | 2.8 | 21028 | 14.8 | 15.36 | 15.92 | 16.48 | 17.04 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8
21 | 3 | 21030 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.52 | 19.24 | 19.96 | 20.68 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 27.12 | 28.24 | 29.36 | 30.48 | 31.6 | 32.92 | 34.24 | 35.56 | 36.88 | 38.2 | 39.68 | 41.16 | 42.64 | 44.12 | 45.6
22 | 0 | 22000 | 10.4 | 10.92 | 11.44 | 11.96 | 12.48 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2
22 | 0.4 | 22004 | 10.4 | 10.92 | 11.44 | 11.96 | 12.48 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2
22 | 0.6 | 22006 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.12 | 16.64 | 17.16 | 17.68 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.52 | 28.44 | 29.36 | 30.28 | 31.2
22 | 0.8 | 22008 | 11.4 | 11.72 | 12.04 | 12.36 | 12.68 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.32 | 17.04 | 17.76 | 18.48 | 19.2 | 19.92 | 20.64 | 21.36 | 22.08 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8
22 | 1 | 22010 | 11.4 | 11.84 | 12.28 | 12.72 | 13.16 | 13.6 | 14.12 | 14.64 | 15.16 | 15.68 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.64 | 30.68 | 31.72 | 32.76 | 33.8
22 | 1.2 | 22012 | 11.4 | 11.92 | 12.44 | 12.96 | 13.48 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.24 | 17.88 | 18.52 | 19.16 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 24.92 | 25.84 | 26.76 | 27.68 | 28.6 | 29.84 | 31.08 | 32.32 | 33.56 | 34.8
22 | 1.4 | 22014 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.32 | 18.04 | 18.76 | 19.48 | 20.2 | 21.04 | 21.88 | 22.72 | 23.56 | 24.4 | 25.44 | 26.48 | 27.52 | 28.56 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4
22 | 1.6 | 22016 | 12 | 12.52 | 13.04 | 13.56 | 14.08 | 14.6 | 15.12 | 15.64 | 16.16 | 16.68 | 17.2 | 17.92 | 18.64 | 19.36 | 20.08 | 20.8 | 21.64 | 22.48 | 23.32 | 24.16 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4
22 | 1.8 | 22018 | 12.4 | 12.84 | 13.28 | 13.72 | 14.16 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.36 | 19.12 | 19.88 | 20.64 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4
22 | 2 | 22020 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 27.24 | 28.48 | 29.72 | 30.96 | 32.2 | 33.36 | 34.52 | 35.68 | 36.84 | 38
22 | 2.2 | 22022 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.12 | 16.64 | 17.16 | 17.68 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.32 | 24.24 | 25.16 | 26.08 | 27 | 28.16 | 29.32 | 30.48 | 31.64 | 32.8 | 34.04 | 35.28 | 36.52 | 37.76 | 39
22 | 2.4 | 22024 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.24 | 16.88 | 17.52 | 18.16 | 18.8 | 19.52 | 20.24 | 20.96 | 21.68 | 22.4 | 23.44 | 24.48 | 25.52 | 26.56 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40
22 | 2.6 | 22026 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.32 | 17.04 | 17.76 | 18.48 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.16 | 30.32 | 31.48 | 32.64 | 33.8 | 35.16 | 36.52 | 37.88 | 39.24 | 40.6
22 | 2.8 | 22028 | 13.6 | 14.12 | 14.64 | 15.16 | 15.68 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.84 | 31.08 | 32.32 | 33.56 | 34.8 | 36.16 | 37.52 | 38.88 | 40.24 | 41.6
22 | 3 | 22030 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.24 | 17.88 | 18.52 | 19.16 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 25.04 | 26.08 | 27.12 | 28.16 | 29.2 | 30.44 | 31.68 | 32.92 | 34.16 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
23 | 0 | 23000 | 9.6 | 10.08 | 10.56 | 11.04 | 11.52 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8
23 | 0.4 | 23004 | 9.6 | 10.08 | 10.56 | 11.04 | 11.52 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8
23 | 0.6 | 23006 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.88 | 15.36 | 15.84 | 16.32 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.28 | 26.16 | 27.04 | 27.92 | 28.8
23 | 0.8 | 23008 | 10.6 | 10.88 | 11.16 | 11.44 | 11.72 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 15.08 | 15.76 | 16.44 | 17.12 | 17.8 | 18.48 | 19.16 | 19.84 | 20.52 | 21.2 | 22.04 | 22.88 | 23.72 | 24.56 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2
23 | 1 | 23010 | 10.6 | 10.96 | 11.32 | 11.68 | 12.04 | 12.4 | 12.88 | 13.36 | 13.84 | 14.32 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.36 | 28.32 | 29.28 | 30.24 | 31.2
23 | 1.2 | 23012 | 10.6 | 11.08 | 11.56 | 12.04 | 12.52 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 15.96 | 16.52 | 17.08 | 17.64 | 18.2 | 18.96 | 19.72 | 20.48 | 21.24 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.56 | 28.72 | 29.88 | 31.04 | 32.2
23 | 1.4 | 23014 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.56 | 20.32 | 21.08 | 21.84 | 22.6 | 23.56 | 24.52 | 25.48 | 26.44 | 27.4 | 28.44 | 29.48 | 30.52 | 31.56 | 32.6
23 | 1.6 | 23016 | 11 | 11.48 | 11.96 | 12.44 | 12.92 | 13.4 | 13.88 | 14.36 | 14.84 | 15.32 | 15.8 | 16.48 | 17.16 | 17.84 | 18.52 | 19.2 | 19.96 | 20.72 | 21.48 | 22.24 | 23 | 23.96 | 24.92 | 25.88 | 26.84 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6
23 | 1.8 | 23018 | 11.6 | 11.96 | 12.32 | 12.68 | 13.04 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.48 | 21.36 | 22.24 | 23.12 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6
23 | 2 | 23020 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 25.16 | 26.32 | 27.48 | 28.64 | 29.8 | 30.84 | 31.88 | 32.92 | 33.96 | 35
23 | 2.2 | 23022 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.88 | 15.36 | 15.84 | 16.32 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.48 | 22.36 | 23.24 | 24.12 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.36 | 32.52 | 33.68 | 34.84 | 36
23 | 2.4 | 23024 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.96 | 15.52 | 16.08 | 16.64 | 17.2 | 17.88 | 18.56 | 19.24 | 19.92 | 20.6 | 21.56 | 22.52 | 23.48 | 24.44 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37
23 | 2.6 | 23026 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 15.08 | 15.76 | 16.44 | 17.12 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.48 | 23.36 | 24.24 | 25.12 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4
23 | 2.8 | 23028 | 12.4 | 12.88 | 13.36 | 13.84 | 14.32 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.56 | 28.72 | 29.88 | 31.04 | 32.2 | 33.44 | 34.68 | 35.92 | 37.16 | 38.4
23 | 3 | 23030 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 15.96 | 16.52 | 17.08 | 17.64 | 18.2 | 18.96 | 19.72 | 20.48 | 21.24 | 22 | 22.96 | 23.92 | 24.88 | 25.84 | 26.8 | 27.96 | 29.12 | 30.28 | 31.44 | 32.6 | 33.84 | 35.08 | 36.32 | 37.56 | 38.8
24 | 0 | 24000 | 8.8 | 9.24 | 9.68 | 10.12 | 10.56 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4
24 | 0.4 | 24004 | 8.8 | 9.24 | 9.68 | 10.12 | 10.56 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4
24 | 0.6 | 24006 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.64 | 14.08 | 14.52 | 14.96 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.48 | 20.16 | 20.84 | 21.52 | 22.2 | 23.04 | 23.88 | 24.72 | 25.56 | 26.4
24 | 0.8 | 24008 | 9.8 | 10.04 | 10.28 | 10.52 | 10.76 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.84 | 14.48 | 15.12 | 15.76 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.32 | 21.04 | 21.76 | 22.48 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6
24 | 1 | 24010 | 9.8 | 10.08 | 10.36 | 10.64 | 10.92 | 11.2 | 11.64 | 12.08 | 12.52 | 12.96 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.08 | 25.96 | 26.84 | 27.72 | 28.6
24 | 1.2 | 24012 | 9.8 | 10.24 | 10.68 | 11.12 | 11.56 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.68 | 15.16 | 15.64 | 16.12 | 16.6 | 17.28 | 17.96 | 18.64 | 19.32 | 20 | 20.84 | 21.68 | 22.52 | 23.36 | 24.2 | 25.28 | 26.36 | 27.44 | 28.52 | 29.6
24 | 1.4 | 24014 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.84 | 15.48 | 16.12 | 16.76 | 17.4 | 18.08 | 18.76 | 19.44 | 20.12 | 20.8 | 21.68 | 22.56 | 23.44 | 24.32 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8
24 | 1.6 | 24016 | 10 | 10.44 | 10.88 | 11.32 | 11.76 | 12.2 | 12.64 | 13.08 | 13.52 | 13.96 | 14.4 | 15.04 | 15.68 | 16.32 | 16.96 | 17.6 | 18.28 | 18.96 | 19.64 | 20.32 | 21 | 21.88 | 22.76 | 23.64 | 24.52 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8
24 | 1.8 | 24018 | 10.8 | 11.08 | 11.36 | 11.64 | 11.92 | 12.2 | 12.8 | 13.4 | 14 | 14.6 | 15.2 | 15.72 | 16.24 | 16.76 | 17.28 | 17.8 | 18.64 | 19.48 | 20.32 | 21.16 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8
24 | 2 | 24020 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 23.08 | 24.16 | 25.24 | 26.32 | 27.4 | 28.32 | 29.24 | 30.16 | 31.08 | 32
24 | 2.2 | 24022 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.64 | 14.08 | 14.52 | 14.96 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.64 | 20.48 | 21.32 | 22.16 | 23 | 23.92 | 24.84 | 25.76 | 26.68 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33
24 | 2.4 | 24024 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.68 | 14.16 | 14.64 | 15.12 | 15.6 | 16.24 | 16.88 | 17.52 | 18.16 | 18.8 | 19.68 | 20.56 | 21.44 | 22.32 | 23.2 | 24.24 | 25.28 | 26.32 | 27.36 | 28.4 | 29.52 | 30.64 | 31.76 | 32.88 | 34
24 | 2.6 | 24026 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.84 | 14.48 | 15.12 | 15.76 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 24.92 | 25.84 | 26.76 | 27.68 | 28.6 | 29.72 | 30.84 | 31.96 | 33.08 | 34.2
24 | 2.8 | 24028 | 11.2 | 11.64 | 12.08 | 12.52 | 12.96 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.28 | 26.36 | 27.44 | 28.52 | 29.6 | 30.72 | 31.84 | 32.96 | 34.08 | 35.2
24 | 3 | 24030 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.68 | 15.16 | 15.64 | 16.12 | 16.6 | 17.28 | 17.96 | 18.64 | 19.32 | 20 | 20.88 | 21.76 | 22.64 | 23.52 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4
25 | 0 | 25000 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23
25 | 0.4 | 25004 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23
25 | 0.6 | 25006 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24
25 | 0.8 | 25008 | 9 | 9.2 | 9.4 | 9.6 | 9.8 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25
25 | 1 | 25010 | 9 | 9.2 | 9.4 | 9.6 | 9.8 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26
25 | 1.2 | 25012 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27
25 | 1.4 | 25014 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 23.8 | 24.6 | 25.4 | 26.2 | 27
25 | 1.6 | 25016 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28
25 | 1.8 | 25018 | 10 | 10.2 | 10.4 | 10.6 | 10.8 | 11 | 11.6 | 12.2 | 12.8 | 13.4 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29
25 | 2 | 25020 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 21 | 22 | 23 | 24 | 25 | 25.8 | 26.6 | 27.4 | 28.2 | 29
25 | 2.2 | 25022 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30
25 | 2.4 | 25024 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
25 | 2.6 | 25026 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27 | 28 | 29 | 30 | 31
25 | 2.8 | 25028 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
25 | 3 | 25030 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Notes:
| 1. |  | 6: Table values were obtained by linear interpolation using CT values published in USEPA's Guidance Manual for Compliance with the Filtration and Disinfection
Requirements for Public Water Systems Using Surface Water Sources, March 1991 edition. This table was developed by Nancy Feagin, P.E. of the
Drinking Water Northwest Regional Office
| 2. |  | 6: For other levels of log inactivation, multiply the table values by the log inactivation required. For example, for 0.5 log inactivation multiply the table values by 0.5.
| 3. |  | 6: For systems with pH values exceeding 9.0 see the Interim Enhanced Surface Water Treatment Rule Notice of Data Availability, Federal Register, November 3, 1997.