## Cover Page & Notes
Washington State Department of Health
Slow Sand Filtration Monthly Report Forms
Notes and Instructions
Version 1.3
Report Designed for All Slow Sand Filtration Plants
|  |  | DOH Form | 331-522-F
|  |  | Revised | 2018-08-27
Notes:
This workbook was developed using Microsoft Excel 2000. However, it can be used in Excel 97 as well as later versions with no problems.
The workbook is intended for use by water treatment plant operators to enhance recordkeeping, reporting and legibility.
It is designed to minimize the work necessary to calculate totals, averages, count events, etc.
The SWTR Disinfection Monthly Reports will also look up and calculate required CT values for Giardia inactivation.
Data or calculations that do not comply with standards or requirements will show up in bold, italic text with pink highlighting.
Saving and Using this Workbook as a Template (Optional)
To save this workbook as a template:
Clear out any data input by the user.
Click on File, Save As. When prompted, give it a new file name, and specify the "Save as type" as Template.
Click on Save in the dialog box.
To use as template when starting a new month:
With Microsoft Excel running, click on File, New. The WTP template should show in the "New" dialog box.
Click on the template; it will come up as a regular Excel spreadsheet.
When the spreadsheet is saved for the first time, you will be required to supply a name for the file.
Recommended file name: "WTP_<PWSID>_<Plant ID>_YYMM.xls", where YYMM is the reporting year and month; e.g.: WTP_00050_001_0308.xls.
The advantage of starting a workbook using a template is that you'll always have a blank workbook (without having to clear out an old one)
and minimize the chance of overwriting a previous month's workbook.
The Forms
The workbook consists of four forms:
The Slow Sand Filtration Monthly Rept is for recording information on the operation of a slow sand filtration plant.
The Slow Sand Filtration - Ripening After Maintenance/Scraping is only to be completed after the filter is scraped or for other significant maintenance events.
The SWTR Monthly Disinfection Rept (DOH Form 331-440-F) is for recording disinfection process information for a plant using Chlorine disinfection.
The Slow Sand Filtration Monthly Summary gathers data from the other two forms, plus other provided information and reports
the SWTR compliance status for the month.
Entering Data:
All cells in the workbook are protected, except for those intended for data input by the user.
Cells and columns intended for user input have titles or headings colored blue.
Printing
Because of the size of the WTP Monthly Rept, it should be printed on legal size paper, in landscape mode, if it is desired to fit on one page.
Use the "Page Setup" menu to choose the paper size and orientation. Change left and right margins to 0.5" and check "Fit to" 1 pg wide by 1 pg tall.
The SWTR Monthly Disinfection Rept and the Monthly Summary each fit on letter size paper in landscape mode.
Where to Send these Report Forms
Send your report forms to the appropriate Office of Drinking Water regional office or as checked below:
| Northwest Drinking Water |  | Southwest Drinking Water |  | Eastern Drinking Water
| Operations |  | Operations |  | Operations
| Department of Health |  | Department of Health |  | Department of Health
| 253-395-6750 |  | 360-236-3030 |  | 509-329-2100
| dw.nwro@doh.wa.gov |  | SWTR.SWRO@doh.wa.gov |  | ero.sw.Treatment.Reports@doh.wa.gov
For Persons with Disabilities
For people with disabilities, this document is available on request in other formats. To submit a request, please call 1-800-525-0127 (TDD/TTY call 711).
Notes on Version 1.2
Added cell for turbidity standards expiration date - Monthly Summary
Notes on Version 1.3
Updated staff contacts
Added optional template for recording required weekly verification checks of on-line turbidimeters.
Disinfection form: Added pop-up note to contact DOH if pH> 9.0 (for instructions on how to calculate CT)
Summary form: Changed minimum recommended sand depth from 18 to 19 inches.
Added line-by-line instructions.

## WTP Monthly Rept
Slow Sand Filter Plant Monthly Report Form
[11 empty] | Month |  | Year
| PWS ID |  |  | PWS Name | [7 empty] | County
| Source ID |  |  | Source Name | [7 empty] | Plant ID
Cells and Columns with Blue Headings are intended for data provided by user
| Meter | Water | Hrs | Chlorine | Filtration Rate |  |  |  | Head Loss |  |  |  | Maxiumum Daily Turbidity (NTU)
Date | Reading | Treated | Operated | Used | (gpm/sq ft) |  |  |  | (inches) |  |  |  | Raw | Filtered Effluent |  |  |  |  | Combined Effluent | Remarks
| (1000 Gal) | (1000 gal) |  | (Lbs) | Filt 1 | Filt 2 | Filt 3 | Filt 4 | Filt 1 | Filt 2 | Filt 3 | Filt 4 |  | Roughing | Filt 1 | Filt 2 | Filt 3 | Filt 4 |  | (See notes below)
Prev*
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total |  | 0 | 0 | 0
Min |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Max |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avg
* Meter reading on last day of previous month
| Total number of CFE samples analyzed for month: N = | [5 empty] | 0 |  | Total number of CFE samples exceeding 1.0 NTU: E = | [6 empty] | 0
| Satisfactory turbidity performance is 95% or greater. Performance determination: [1-(E/N)]x100 = | [14 empty] | Report Submitted By
| Number of days CFE exceeded 5.0 NTU this month: | [5 empty] | 0 | [8 empty] | Signature
| Notes: | Record date(s) when filter is off-line for scraping
|  | Record filter ripening data on supplemental form | [11 empty] | See Cover Page for information on where to send this form.

## Ripening Form
Slow Sand Filtration
Ripening After Maintenance/Scraping Form
*Please complete one form for each maintenance event (scraping, resanding, etc.).
Complete this form only in months in which there were maintenance events.
PWS ID | 0 |  | Source ID | 0 |  | Month | 0 | Year | 0
PWS Name | 0 |  |  | Source Name |  | 0
|  |  |  | Plant ID | 0 |  | County | 0
Filter Number:
Type of Maintenance:
Dates maintenance was performed:
Filter off line (date):
Filter returned to service (date):
Hours (or days) of filter-to-waste:
Sand depth prior to service (in):
Sand depth remaining (in):
Monitoring After Maintenanace/Scraping
| Date | Filtration Rate (gpm/ sq. ft.) | Outlet Turbidity (NTU) | Total Coliform, Raw (#/100 mL) | Total Coliform, Filtered (#/100 mL) | Filter-to-Waste (Y/N)
Notes:
In some cases, only a few days of monitoring after a maintenance event is necessary, in other cases it may be much longer.
Report Submitted By
Signature

## Online Turb Verification
Weekly Verification Checks-Online Turbidimeters
PWS Name | 0
PWS ID | 0
WEEK 1 (date): |  | Operator Name: |  |  |  | WEEK 2 (date): |  | Operator Name:
Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action | Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action
Example: IFE-FILTER #1/HACH 1720E | 0.08 | 0.08 | 0.09 | Y | none | Example: CFE/HACH 1720E | 0.13 | 0.14 | 0.05 | N | Recalibrated on-line
|  |  |  | * or 10% for the raw | [5 empty] | * or 10% for the raw
WEEK 3 (date): |  | Operator Name: |  |  |  | WEEK 4 (date): |  | Operator Name:
Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action | Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action
* or 10% for the raw
WEEK 5 (date): |  | Operator Name:
Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action
* or 10% for the raw

## SWTR Monthly Disinfection Rept
Washington State Department of Health
SWTR Disinfection Monthly Report Form
| PWS ID | 0 |  | PWS Name | 0 |  |  |  | Month | 0 | Year | 0
| County | 0 | [5 empty] | Submitted By
| Source ID | 0 |  | Source Name | 0 |  | . | WTPO Cert No
| Plant ID | 0 | [5 empty] | Telephone No
Population Served |  |  |  |  | Min Grab Samples Reqd | 1 | Residuals Normally Measured Continuously Y/N
Overall Log Treatment Req'd |  |  | 3 |  | Filtration Log Removal Credit |  |  | 2 |  | Required Disinfection Log Reduction |  |  |  | 1
Cells and Columns with Blue Headings are intended for data provided by user
|  |  | Inactivation Ratio Determination | [7 empty] | Disinfectant Residual at |  |  | Residual in
Note: For correct results, remember to enter your plant's Filtration Log Removal Credit in cell I9 above | [10 empty] | Distribution Entry Point |  |  | Distribution System
Date | Peak Hour Flow gpm | Water Temp C | pH | Chlorine Residual {C} mg/L | Tank Level ft (must be at least __ft) | Contact Time {T} minutes | Calculated CT {C*T} | Required CT from Tables* | Inact Ratio {Calc CT/Req'd CT} | No. of Samples Collected "C" if Continuous | Lowest Daily Residual mg/L | Duration less than 0.2mg/L hours | DOH Notified? Name & Time | No of Sites Sampled | Minimum Residual mg/L | No of Samples Residual Not Detected
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | [9 empty] | 0 | # < 0.2 mg/L | # > 4 hrs |  | 0 |  | 0
Count | [8 empty] | 0 |  | 0 | 0
Min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Max | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Avg
| *Adjusted for Log Reduction Required |  |  |  |  | No. Days Inact Ratio < 1 |  | 0
DOH Form 331-440-F (Excel version) | [9 empty] | Signature

## Req'd CT Calc (hidden)
| 0 | 501 | 1001 | 2501 | 3301 |  |  |  | 0 | 6 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5 | 6.6 | 6.7 | 6.8 | 6.9 | 7 | 7.1 | 7.2 | 7.3 | 7.4 | 7.5 | 7.6 | 7.7 | 7.8 | 7.9 | 8 | 8.1 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 8.7 | 8.8 | 8.9 | 9
| 1 | 2 | 3 | 4 | 6 |  |  |  | 2 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
| PopServed | 0 |  |  | MinGrab | 1
|  |  | Inactivation Ratio Determination | [5 empty] | 0 2: Disinfection Log Reduction Req'd; 6.3 5: 1
Date | Peak Hour Flow gpm | Water Temp C | pH | Chlorine Residual {C} mg/L | Contact Time {T} minutes | Calculated CT {C*T} | Required CT from Tables | Inact Ratio {Calc CT/Req'd CT} | 0 2: Temp Adj; 6 2: pH Offset; 6.1 3: Chlorine Adj; 6.2 4: CT; 6.3 5: CT Calc; 6.4 6: Table Lookup; 6.5 7: CT Required; 6.6 8: Inact Ratio; 6.8 10: Lowest Daily Residual mg/L; 6.9 11: Duration less than 0.2mg/L hours; 7 12: Valid Durations hours
1 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
2 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
3 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
4 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
5 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
6 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
7 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
8 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
9 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
10 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
11 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
12 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
13 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
14 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
15 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
16 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
17 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
18 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
19 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
20 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
21 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
22 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
23 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
24 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
25 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
26 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
27 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
28 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
29 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
30 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
31 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
Total
Count | [8 empty] | 7 12: 0
Min | [8 empty] | 6.8 10: 0; 6.9 11: 0; 7 12: 0
Max | [8 empty] | 6.8 10: 0; 6.9 11: 0; 7 12: 0
Avg
| ADAM | 3
| ASOT | 3
| BENT | 3
| CHEL | 3
| CLAL | 2
| CLAR | 2
| CLIC | 3
| COLO | 3
| COLU | 3
| COWL | 2
| DOUG | 3
| FERR | 3
| FRAN | 3
| GARF | 3
| GRAN | 3
| GRAY | 2
| ILAN | 1
| ISLA | 1
| JEFF | 2
| KING | 1
| KITI | 3
| KITS | 2
| KITT | 3
| KLIC | 3
| KOWL | 2
| LEWI | 2
| LINC | 3
| MASI | 2
| MASO | 2
| OKAN | 3
| OKON | 3
| PACI | 2
| PEIR | 1
| PEND | 3
| PIER | 1
| POND | 3
| SAN | 1
| SANJ | 1
| SKAG | 1
| SKAM | 2
| SNOH | 1
| SPOK | 3
| STEV | 3
| THUR | 2
| TURS | 2
| WALL | 3
| WATC | 1
| WHAT | 1
| WHIT | 3
| WITM | 3
| YAKA | 3
| YAKI | 3

## Monthly Summary
Surface Water Treatment Plant
Slow Sand Filtration Monthly Report Summary Form
PWS ID | 0 |  | Source ID | 0 |  | Month | 0 | Year | 0
PWS Name | 0 |  |  | Source Name |  | 0
|  |  |  | Plant ID | 0 |  | County | 0
|  | Color code for form information: | WTP Monthly Rept |  | SWTR Monthly Disinfection Rept |  |  | To be supplied by user
Source (Raw) Water | 1. Maximum density of raw water fecal coliform (# organisms/100 ml)
| 2. Maximum turbidity of the raw water treated by the plant (NTU) | [7 empty] | 0
Filtration | 3. Was there continuous flow through the filter(s) this month? | [6 empty] | Y/N:
| 4. Number of filtered water turbidity measurements taken | [7 empty] | 0
| 5. Turbidity performance limit |  | 1 | No. of filtered measurements > performance limit |  |  |  |  | 0
| 6. Max. allowable turbidity |  | 5 | No. of days finished water measurements > max allowable limit: |  |  |  |  | 0
| 7. Maximum filtered water turbidity (NTU) | [7 empty] | 0
| 8. Was unfiltered water provided to consumers at any time? | [6 empty] | Y/N:
| 9. Filter(s) scraped this month? |  |  |  |  | (Use supplemental form) |  | Y/N:
| 10. Is there at least 19 inches depth of sand left in each filter? | [6 empty] | Y/N:
| 11. Approved filtration rate (gpm/sf): | [6 empty] | Max. operational filt. rate (gpm/sf):
12. Maximum flow rate treated (gpm):
Inactivation Ratio | 13. Number of days disinfectant CT was monitored this month | [7 empty] | 0
| 14. Number of days inactivation ratio was below 1.0 (Enter 0 if none) | [7 empty] | 0
| 15. Lowest daily inactivation ratio this month | [7 empty] | 0
Distribution Entry Point Samples | 16. Number of days during which plant produced water this month | [7 empty] | 0
| 17. Number of entry point residual samples analyzed this month | [7 empty] | 0
| 18. Number of days when residual fell below 0.2 mg/l (Enter 0 if none) | [7 empty] | 0
| 19. Number of days when residual fell below 0.2 mg/l for more than 4 hours (Enter 0 if none) | [7 empty] | 0
Distribution System Residuals | 20. Number of days water served to public this month
21. Number of days distribution system disinfectant residual was monitored
| 22. Number of distribution system disinfectant residual samples measured this month | [7 empty] | 0
| 23. Number of samples where no disinfectant residual was detected (Enter 0 if none) | [7 empty] | 0
24. Average of all disinfectant residual measurements taken with coliform samples
Finished Water/ General | 25. Number of water quality complaints received from consumers served by system
| 26. Were req'd samples (pH, temp, turb, residuals) taken only by the certified operator? | [6 empty] | Y/N:
| 27. Were all turbidimeters calibrated w/ primary standard within last quarter? Date | [6 empty] | Y/N:
Primary standard expiration date:
| 28. Critical alarms tested? Remarks: |  |  |  |  | Date |  | Y/N:
Report Submitted By | [5 empty] | WTPO Cert No
Signature | [5 empty] | Telephone Number
See Cover Page for information on where to send this form.

## Line-by-line instructions
Line-by-Line Instructions
General Reminder: Cells and columns intended for user input have titles or headings colored blue.
Slow Sand WTP Monthly Rept
Column | Comment
Water Treated (1000 gal) | Automatically calculated from meter readings. Include all water treated, including filter-to-waste.
Total Hours of Operation | You can determine this using SCADA, a chart recorder, a plant run time meter, or estimate using the total volume produced divided by the known (fixed) plant flow rate
Chlorine Used (lbs) | (liquid) lbs/day=lbs/gal x gal/day lbs/gal=(% Solution/100) x 8.34 lbs/gal x specific gravity
Turbidity Raw | If monitoring continuously, record the daily average value. If using grab samples, collect representative sample(s) daily.
Remarks | Record anything unusual or out-of-the-ordinary.
Ripening Form
This is a template for recording the slow sand ripening data following maintenance or scraping of a filter. For more information see "Slow Sand Filtration: Recommended Operations and Optimization Goals" (DOH Pub 331-601).
Online Turb Verification
Use this template to record the required weekly verification checks of your online turbidimeters. You do not need to use it if you already have a system in place to record this information. Keep this on file. It is not necessary to submit it unless the department requests it.
SWTR Monthly Disinfection Report
Column | Comment
Peak hourly flow (PHF) | This is the maximum one-hour flow through the contact basin, expressed in gallons per minute. It is not the peak instantaneous flow. Use the flow into or out of the contact basin, whichever is higher. For most systems, this is the flow leaving the contact basin.
Water temperature | Measure during PHF at the same location as chlorine residual (for CT). May also report daily minimum if you have continuous measurement.
pH | Measure during PHF at the same location as chlorine residual (for CT). May also report daily maximum if you have continuous measurement. Call your DOH regional office for instructions if your pH exceeds 9.0
Chlorine Residual (CT) | Measure the free chlorine residual at the end of the contact basin or pipe, prior to the first customer, during PHF. May also report daily minimum if you have continuous measurement.
Tank Level | If you use a storage tank or clearwell for contact time, record the tank level during peak hourly flow. May also report the daily minimum tank level. In the column header, record the assumed minimum tank level, if any, used for your CT calculation.
Contact Time | Calculate this every day (not at the end of the month). Use PHF and your DOH-approved CT calculation.
Inact Ratio | This calculates automatically based on the numbers you enter. Call your DOH regional office immediately if the value drops below 1.0
Entry Point-Lowest Daily Residual mg/L | Systems serving more than 3300 people must monitor continuously & report the lowest absolute value for the day. If continuous equipment fails, you must take grab samples every four hours and have equipment back up and running with five working days. Systems serving less than 3300 people may use grab samples (1-4 per day depending on population) Systems using grab sampling, take one sample at PHF and the remaining samples spaced over the period that the plant produces water. Record the lowest grab sample result. Call your DOH regional office immediately if this value drops below 0.2 mg/L
Entry Point-Duration less than 0.2 mg/L hours | Enter the total length of time that the residual was below 0.2 mg/L.
DOH Notified? Name & Time | Each day the residual was below 0.2 mg/L write the date and the name of the person you reported to at DOH
Distribution-No of Sites Sampled | Measure distribution residual at least once per day and at the same time and location as coliform samples. Measure from representative locations throughout the distribution system.
Minimum Residual mg/L | Record the lowest free chlorine residual for the day. Systems using chloramines: record the combined chlorine residual.
No of Samples Residual Not Detected | Systems that use heterotrophic plate counts (HPC): an HPC level less than or equal to 500 organisms/mL is considered to have a detectable residual disinfectant concentration. For systems that do not use HPC, "detectable residual disinfectant concentration" means 0.2 mg/L free chlorine, total chlorine or combined chlorine. The department may approve a written request to use a lower value. At a minimum, the request to use a lower value must identify the instrument used to measure the residual disinfectant concentration and include the manufacturer's documentation on the instrument's accuracy to measure the lower value.
Monthly Summary
All blanks must be completed each month. If a question does not apply to your system, please check the n/a box.
Item # | Comment
1 | WAC 246-290-664(1)
2 | Maximum raw water turbidity-Maximum of the reported daily values for the month. (populates automatically)
3 | Don't include filters off-line for scraping, ripening or other maintenance. Flow must be maintained through the filter to provide food for the microorganisms. Short term dewatering is acceptable only to scrape the filters.
4 | Filtered water turbidity measurements reported for the combined filter effluent from the treatment plant. (populates automatically)
5 & 6 | The turbidity performance limit for slow sand filtration is 1.0 NTU and the maximum allowable turbidity is 5.0 NTU.
8 | Specifically, was any unfiltered surface water or GWI water provided, not from an alternate source such as wells.
9 | Record filter cleaning and ripening data on "Ripening Form"
10 | When the depth of sand approaches 19", make plans to re-sand the filters.
23 | Disinfectant Residuals - A heterotrophic plate count (HPC) level less than or equal to 500 organisms/mL is considered to have a detectable residual disinfectant concentration.
24 | This question is to help meet a DBP rule requirement: systems must measure and report the average value each month of the residual disinfectant level at the same time/location as coliform samples. Subpart H (surface water) systems have the option of using the results of the daily distribution samples - this option should be specified in your DBP monitoring plan. If you have opted to use the daily distribution samples, enter that average here.
26 | Analytical Measurements - Only qualified persons (such as certified operators) shall conduct measurements for pH, temperature, turbidity, and residual disinfectant concentrations. See WAC 246-290-638(1) for details.
27 | Turbidimeter Calibration - Calibrate turbidity equipment based upon a primary standard on at least a quarterly basis for instruments using an incandescent light source and on at least an annual basis for instruments using an LED or laser light source. If there are more than one and they were calibrated on different dates, enter the earliest calibration date. WAC 246-290-638(4)
28 | Critical alarms are those alarms that monitor a critical treatment process such as filtration or disinfection where treatment failure poses an immediate risk to public health and/or safety. For plants that run in an unattended mode, these alarms must trigger plant shutdown, not just dial out to the on-call operator. Recommended testing frequency: Plants staffed 24/7 (quarterly), Plants that operate some of the time unattended (monthly), Plants with a history of reliability problems (weekly)
Signature | The operator in responsible charge with the appropriate level of certification (at or above the plant rating) must sign this form.

## CT Lookup Table (hidden)
Look-up Table for Required CT for 1 log Reduction in Giardia at Various Temperatures, Chlorine Concentration and pH
Temp | Chlorine | Lookup | [6 empty] | pH | [17 empty] | pH
Degrees | Conc | Row
C | (mg/l) |  | 6 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5 | 6.6 | 6.7 | 6.8 | 6.9 | 7 | 7.1 | 7.2 | 7.3 | 7.4 | 7.5 | 7.6 | 7.7 | 7.8 | 7.9 | 8 | 8.1 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 8.7 | 8.8 | 8.9 | 9
0 | 0 | 0 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0 | 500 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0.4 | 504 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0.6 | 506 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.6 | 72.2 | 74.8 | 77.4 | 80 | 83 | 86 | 89 | 92 | 95 | 98.8 | 102.6 | 106.4 | 110.2 | 114 | 118.4 | 122.8 | 127.2 | 131.6 | 136
0.5 | 0.8 | 508 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.8 | 73.6 | 76.4 | 79.2 | 82 | 85.2 | 88.4 | 91.6 | 94.8 | 98 | 102 | 106 | 110 | 114 | 118 | 122.6 | 127.2 | 131.8 | 136.4 | 141
0.5 | 1 | 510 | 49 | 51 | 53 | 55 | 57 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.4 | 90.8 | 94.2 | 97.6 | 101 | 105.2 | 109.4 | 113.6 | 117.8 | 122 | 126.8 | 131.6 | 136.4 | 141.2 | 146
0.5 | 1.2 | 512 | 51 | 52.8 | 54.6 | 56.4 | 58.2 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86 | 89.6 | 93.2 | 96.8 | 100.4 | 104 | 108.2 | 112.4 | 116.6 | 120.8 | 125 | 130 | 135 | 140 | 145 | 150
0.5 | 1.4 | 514 | 52 | 53.8 | 55.6 | 57.4 | 59.2 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.6 | 96.2 | 99.8 | 103.4 | 107 | 111.4 | 115.8 | 120.2 | 124.6 | 129 | 134.2 | 139.4 | 144.6 | 149.8 | 155
0.5 | 1.6 | 516 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63 | 65.4 | 67.8 | 70.2 | 72.6 | 75 | 78.2 | 81.4 | 84.6 | 87.8 | 91 | 94.8 | 98.6 | 102.4 | 106.2 | 110 | 114.4 | 118.8 | 123.2 | 127.6 | 132 | 137.4 | 142.8 | 148.2 | 153.6 | 159
0.5 | 1.8 | 518 | 54 | 56 | 58 | 60 | 62 | 64 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 80.2 | 83.4 | 86.6 | 89.8 | 93 | 97 | 101 | 105 | 109 | 113 | 117.6 | 122.2 | 126.8 | 131.4 | 136 | 141.4 | 146.8 | 152.2 | 157.6 | 163
0.5 | 2 | 520 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 82.2 | 85.4 | 88.6 | 91.8 | 95 | 99 | 103 | 107 | 111 | 115 | 119.8 | 124.6 | 129.4 | 134.2 | 139 | 144.6 | 150.2 | 155.8 | 161.4 | 167
0.5 | 2.2 | 522 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.6 | 88.2 | 91.8 | 95.4 | 99 | 102.8 | 106.6 | 110.4 | 114.2 | 118 | 122.8 | 127.6 | 132.4 | 137.2 | 142 | 147.6 | 153.2 | 158.8 | 164.4 | 170
0.5 | 2.4 | 524 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.8 | 73.6 | 76.4 | 79.2 | 82 | 85.4 | 88.8 | 92.2 | 95.6 | 99 | 103.2 | 107.4 | 111.6 | 115.8 | 120 | 125 | 130 | 135 | 140 | 145 | 150.8 | 156.6 | 162.4 | 168.2 | 174
0.5 | 2.6 | 526 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.4 | 90.8 | 94.2 | 97.6 | 101 | 105.4 | 109.8 | 114.2 | 118.6 | 123 | 128 | 133 | 138 | 143 | 148 | 154 | 160 | 166 | 172 | 178
0.5 | 2.8 | 528 | 59 | 61.4 | 63.8 | 66.2 | 68.6 | 71 | 74 | 77 | 80 | 83 | 86 | 89.4 | 92.8 | 96.2 | 99.6 | 103 | 107.4 | 111.8 | 116.2 | 120.6 | 125 | 130.2 | 135.4 | 140.6 | 145.8 | 151 | 157 | 163 | 169 | 175 | 181
0.5 | 3 | 530 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 75 | 78 | 81 | 84 | 87 | 90.6 | 94.2 | 97.8 | 101.4 | 105 | 109.4 | 113.8 | 118.2 | 122.6 | 127 | 132.2 | 137.4 | 142.6 | 147.8 | 153 | 159.2 | 165.4 | 171.6 | 177.8 | 184
1 | 0 | 1000 | 44.4444 | 46.0222 | 47.6 | 49.1778 | 50.7556 | 52.3333 | 54.4444 | 56.5556 | 58.6667 | 60.7778 | 62.8889 | 65.5778 | 68.2667 | 70.9556 | 73.6444 | 76.3333 | 78.8889 | 81.4444 | 84 | 86.5556 | 89.1111 | 92.6 | 96.0889 | 99.5778 | 103.0667 | 106.5556 | 110.4222 | 114.2889 | 118.1556 | 122.0222 | 125.8889
1 | 0.4 | 1004 | 44.4444 | 46.0222 | 47.6 | 49.1778 | 50.7556 | 52.3333 | 54.4444 | 56.5556 | 58.6667 | 60.7778 | 62.8889 | 65.5778 | 68.2667 | 70.9556 | 73.6444 | 76.3333 | 78.8889 | 81.4444 | 84 | 86.5556 | 89.1111 | 92.6 | 96.0889 | 99.5778 | 103.0667 | 106.5556 | 110.4222 | 114.2889 | 118.1556 | 122.0222 | 125.8889
1 | 0.6 | 1006 | 45.4444 | 47.2 | 48.9556 | 50.7111 | 52.4667 | 54.2222 | 56.3556 | 58.4889 | 60.6222 | 62.7556 | 64.8889 | 67.4 | 69.9111 | 72.4222 | 74.9333 | 77.4444 | 80.3556 | 83.2667 | 86.1778 | 89.0889 | 92 | 95.6667 | 99.3333 | 103 | 106.6667 | 110.3333 | 114.6 | 118.8667 | 123.1333 | 127.4 | 131.6667
1 | 0.8 | 1008 | 46.4444 | 48.2 | 49.9556 | 51.7111 | 53.4667 | 55.2222 | 57.3556 | 59.4889 | 61.6222 | 63.7556 | 65.8889 | 68.5778 | 71.2667 | 73.9556 | 76.6444 | 79.3333 | 82.4444 | 85.5556 | 88.6667 | 91.7778 | 94.8889 | 98.7556 | 102.6222 | 106.4889 | 110.3556 | 114.2222 | 118.6667 | 123.1111 | 127.5556 | 132 | 136.4444
1 | 1 | 1010 | 47.4444 | 49.3778 | 51.3111 | 53.2444 | 55.1778 | 57.1111 | 59.2444 | 61.3778 | 63.5111 | 65.6444 | 67.7778 | 70.4889 | 73.2 | 75.9111 | 78.6222 | 81.3333 | 84.6222 | 87.9111 | 91.2 | 94.4889 | 97.7778 | 101.8444 | 105.9111 | 109.9778 | 114.0444 | 118.1111 | 122.7556 | 127.4 | 132.0444 | 136.6889 | 141.3333
1 | 1.2 | 1012 | 49.3333 | 51.0667 | 52.8 | 54.5333 | 56.2667 | 58 | 60.3333 | 62.6667 | 65 | 67.3333 | 69.6667 | 72.3778 | 75.0889 | 77.8 | 80.5111 | 83.2222 | 86.7111 | 90.2 | 93.6889 | 97.1778 | 100.6667 | 104.7333 | 108.8 | 112.8667 | 116.9333 | 121 | 125.8444 | 130.6889 | 135.5333 | 140.3778 | 145.2222
1 | 1.4 | 1014 | 50.2222 | 51.9778 | 53.7333 | 55.4889 | 57.2444 | 59 | 61.5111 | 64.0222 | 66.5333 | 69.0444 | 71.5556 | 74.4444 | 77.3333 | 80.2222 | 83.1111 | 86 | 89.5111 | 93.0222 | 96.5333 | 100.0444 | 103.5556 | 107.8 | 112.0444 | 116.2889 | 120.5333 | 124.7778 | 129.8222 | 134.8667 | 139.9111 | 144.9556 | 150
1 | 1.6 | 1016 | 50.3333 | 52.4444 | 54.5556 | 56.6667 | 58.7778 | 60.8889 | 63.2222 | 65.5556 | 67.8889 | 70.2222 | 72.5556 | 75.6444 | 78.7333 | 81.8222 | 84.9111 | 88 | 91.6667 | 95.3333 | 99 | 102.6667 | 106.3333 | 110.6222 | 114.9111 | 119.2 | 123.4889 | 127.7778 | 132.9778 | 138.1778 | 143.3778 | 148.5778 | 153.7778
1 | 1.8 | 1018 | 52.2222 | 54.1556 | 56.0889 | 58.0222 | 59.9556 | 61.8889 | 64.4 | 66.9111 | 69.4222 | 71.9333 | 74.4444 | 77.5333 | 80.6222 | 83.7111 | 86.8 | 89.8889 | 93.7556 | 97.6222 | 101.4889 | 105.3556 | 109.2222 | 113.6889 | 118.1556 | 122.6222 | 127.0889 | 131.5556 | 136.7778 | 142 | 147.2222 | 152.4444 | 157.6667
1 | 2 | 1020 | 53.2222 | 55.3333 | 57.4444 | 59.5556 | 61.6667 | 63.7778 | 66.2889 | 68.8 | 71.3111 | 73.8222 | 76.3333 | 79.4444 | 82.5556 | 85.6667 | 88.7778 | 91.8889 | 95.7556 | 99.6222 | 103.4889 | 107.3556 | 111.2222 | 115.8667 | 120.5111 | 125.1556 | 129.8 | 134.4444 | 139.8667 | 145.2889 | 150.7111 | 156.1333 | 161.5556
1 | 2.2 | 1022 | 54.1111 | 56.2444 | 58.3778 | 60.5111 | 62.6444 | 64.7778 | 67.4667 | 70.1556 | 72.8444 | 75.5333 | 78.2222 | 81.6889 | 85.1556 | 88.6222 | 92.0889 | 95.5556 | 99.2667 | 102.9778 | 106.6889 | 110.4 | 114.1111 | 118.7556 | 123.4 | 128.0444 | 132.6889 | 137.3333 | 142.7556 | 148.1778 | 153.6 | 159.0222 | 164.4444
1 | 2.4 | 1024 | 55.1111 | 57.2444 | 59.3778 | 61.5111 | 63.6444 | 65.7778 | 68.4667 | 71.1556 | 73.8444 | 76.5333 | 79.2222 | 82.5333 | 85.8444 | 89.1556 | 92.4667 | 95.7778 | 99.8222 | 103.8667 | 107.9111 | 111.9556 | 116 | 120.8444 | 125.6889 | 130.5333 | 135.3778 | 140.2222 | 145.8444 | 151.4667 | 157.0889 | 162.7111 | 168.3333
1 | 2.6 | 1026 | 56.1111 | 58.4222 | 60.7333 | 63.0444 | 65.3556 | 67.6667 | 70.3556 | 73.0444 | 75.7333 | 78.4222 | 81.1111 | 84.4222 | 87.7333 | 91.0444 | 94.3556 | 97.6667 | 101.9111 | 106.1556 | 110.4 | 114.6444 | 118.8889 | 123.7333 | 128.5778 | 133.4222 | 138.2667 | 143.1111 | 148.9111 | 154.7111 | 160.5111 | 166.3111 | 172.1111
1 | 2.8 | 1028 | 57 | 59.3111 | 61.6222 | 63.9333 | 66.2444 | 68.5556 | 71.4444 | 74.3333 | 77.2222 | 80.1111 | 83 | 86.3111 | 89.6222 | 92.9333 | 96.2444 | 99.5556 | 103.8222 | 108.0889 | 112.3556 | 116.6222 | 120.8889 | 125.9111 | 130.9333 | 135.9556 | 140.9778 | 146 | 151.8 | 157.6 | 163.4 | 169.2 | 175
1 | 3 | 1030 | 58 | 60.3111 | 62.6222 | 64.9333 | 67.2444 | 69.5556 | 72.4667 | 75.3778 | 78.2889 | 81.2 | 84.1111 | 87.6 | 91.0889 | 94.5778 | 98.0667 | 101.5556 | 105.8 | 110.0444 | 114.2889 | 118.5333 | 122.7778 | 127.8222 | 132.8667 | 137.9111 | 142.9556 | 148 | 154 | 160 | 166 | 172 | 178
2 | 0 | 2000 | 41.3333 | 42.8667 | 44.4 | 45.9333 | 47.4667 | 49 | 50.9333 | 52.8667 | 54.8 | 56.7333 | 58.6667 | 61.1333 | 63.6 | 66.0667 | 68.5333 | 71 | 73.4667 | 75.9333 | 78.4 | 80.8667 | 83.3333 | 86.6 | 89.8667 | 93.1333 | 96.4 | 99.6667 | 103.2667 | 106.8667 | 110.4667 | 114.0667 | 117.6667
2 | 0.4 | 2004 | 41.3333 | 42.8667 | 44.4 | 45.9333 | 47.4667 | 49 | 50.9333 | 52.8667 | 54.8 | 56.7333 | 58.6667 | 61.1333 | 63.6 | 66.0667 | 68.5333 | 71 | 73.4667 | 75.9333 | 78.4 | 80.8667 | 83.3333 | 86.6 | 89.8667 | 93.1333 | 96.4 | 99.6667 | 103.2667 | 106.8667 | 110.4667 | 114.0667 | 117.6667
2 | 0.6 | 2006 | 42.3333 | 44 | 45.6667 | 47.3333 | 49 | 50.6667 | 52.6667 | 54.6667 | 56.6667 | 58.6667 | 60.6667 | 63 | 65.3333 | 67.6667 | 70 | 72.3333 | 75.0667 | 77.8 | 80.5333 | 83.2667 | 86 | 89.4 | 92.8 | 96.2 | 99.6 | 103 | 107 | 111 | 115 | 119 | 123
2 | 0.8 | 2008 | 43.3333 | 45 | 46.6667 | 48.3333 | 50 | 51.6667 | 53.6667 | 55.6667 | 57.6667 | 59.6667 | 61.6667 | 64.1333 | 66.6 | 69.0667 | 71.5333 | 74 | 76.9333 | 79.8667 | 82.8 | 85.7333 | 88.6667 | 92.2667 | 95.8667 | 99.4667 | 103.0667 | 106.6667 | 110.8 | 114.9333 | 119.0667 | 123.2 | 127.3333
2 | 1 | 2010 | 44.3333 | 46.1333 | 47.9333 | 49.7333 | 51.5333 | 53.3333 | 55.3333 | 57.3333 | 59.3333 | 61.3333 | 63.3333 | 65.8667 | 68.4 | 70.9333 | 73.4667 | 76 | 79.0667 | 82.1333 | 85.2 | 88.2667 | 91.3333 | 95.1333 | 98.9333 | 102.7333 | 106.5333 | 110.3333 | 114.6667 | 119 | 123.3333 | 127.6667 | 132
2 | 1.2 | 2012 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.5333 | 70.0667 | 72.6 | 75.1333 | 77.6667 | 80.9333 | 84.2 | 87.4667 | 90.7333 | 94 | 97.8 | 101.6 | 105.4 | 109.2 | 113 | 117.5333 | 122.0667 | 126.6 | 131.1333 | 135.6667
2 | 1.4 | 2014 | 46.6667 | 48.3333 | 50 | 51.6667 | 53.3333 | 55 | 57.3333 | 59.6667 | 62 | 64.3333 | 66.6667 | 69.3333 | 72 | 74.6667 | 77.3333 | 80 | 83.3333 | 86.6667 | 90 | 93.3333 | 96.6667 | 100.6 | 104.5333 | 108.4667 | 112.4 | 116.3333 | 121.0667 | 125.8 | 130.5333 | 135.2667 | 140
2 | 1.6 | 2016 | 47 | 48.9333 | 50.8667 | 52.8 | 54.7333 | 56.6667 | 58.8667 | 61.0667 | 63.2667 | 65.4667 | 67.6667 | 70.5333 | 73.4 | 76.2667 | 79.1333 | 82 | 85.4 | 88.8 | 92.2 | 95.6 | 99 | 103.0667 | 107.1333 | 111.2 | 115.2667 | 119.3333 | 124.1333 | 128.9333 | 133.7333 | 138.5333 | 143.3333
2 | 1.8 | 2018 | 48.6667 | 50.4667 | 52.2667 | 54.0667 | 55.8667 | 57.6667 | 60 | 62.3333 | 64.6667 | 67 | 69.3333 | 72.2 | 75.0667 | 77.9333 | 80.8 | 83.6667 | 87.2667 | 90.8667 | 94.4667 | 98.0667 | 101.6667 | 105.8667 | 110.0667 | 114.2667 | 118.4667 | 122.6667 | 127.5333 | 132.4 | 137.2667 | 142.1333 | 147
2 | 2 | 2020 | 49.6667 | 51.6 | 53.5333 | 55.4667 | 57.4 | 59.3333 | 61.6667 | 64 | 66.3333 | 68.6667 | 71 | 73.9333 | 76.8667 | 79.8 | 82.7333 | 85.6667 | 89.2667 | 92.8667 | 96.4667 | 100.0667 | 103.6667 | 108 | 112.3333 | 116.6667 | 121 | 125.3333 | 130.4 | 135.4667 | 140.5333 | 145.6 | 150.6667
2 | 2.2 | 2022 | 50.3333 | 52.3333 | 54.3333 | 56.3333 | 58.3333 | 60.3333 | 62.8 | 65.2667 | 67.7333 | 70.2 | 72.6667 | 75.8667 | 79.0667 | 82.2667 | 85.4667 | 88.6667 | 92.2 | 95.7333 | 99.2667 | 102.8 | 106.3333 | 110.6667 | 115 | 119.3333 | 123.6667 | 128 | 133.0667 | 138.1333 | 143.2 | 148.2667 | 153.3333
2 | 2.4 | 2024 | 51.3333 | 53.3333 | 55.3333 | 57.3333 | 59.3333 | 61.3333 | 63.8 | 66.2667 | 68.7333 | 71.2 | 73.6667 | 76.8 | 79.9333 | 83.0667 | 86.2 | 89.3333 | 93.0667 | 96.8 | 100.5333 | 104.2667 | 108 | 112.5333 | 117.0667 | 121.6 | 126.1333 | 130.6667 | 135.9333 | 141.2 | 146.4667 | 151.7333 | 157
2 | 2.6 | 2026 | 52.3333 | 54.4667 | 56.6 | 58.7333 | 60.8667 | 63 | 65.4667 | 67.9333 | 70.4 | 72.8667 | 75.3333 | 78.4667 | 81.6 | 84.7333 | 87.8667 | 91 | 94.9333 | 98.8667 | 102.8 | 106.7333 | 110.6667 | 115.2 | 119.7333 | 124.2667 | 128.8 | 133.3333 | 138.7333 | 144.1333 | 149.5333 | 154.9333 | 160.3333
2 | 2.8 | 2028 | 53 | 55.1333 | 57.2667 | 59.4 | 61.5333 | 63.6667 | 66.3333 | 69 | 71.6667 | 74.3333 | 77 | 80.1333 | 83.2667 | 86.4 | 89.5333 | 92.6667 | 96.6667 | 100.6667 | 104.6667 | 108.6667 | 112.6667 | 117.3333 | 122 | 126.6667 | 131.3333 | 136 | 141.4 | 146.8 | 152.2 | 157.6 | 163
2 | 3 | 2030 | 54 | 56.1333 | 58.2667 | 60.4 | 62.5333 | 64.6667 | 67.4 | 70.1333 | 72.8667 | 75.6 | 78.3333 | 81.6 | 84.8667 | 88.1333 | 91.4 | 94.6667 | 98.6 | 102.5333 | 106.4667 | 110.4 | 114.3333 | 119.0667 | 123.8 | 128.5333 | 133.2667 | 138 | 143.6 | 149.2 | 154.8 | 160.4 | 166
3 | 0 | 3000 | 38.2222 | 39.7111 | 41.2 | 42.6889 | 44.1778 | 45.6667 | 47.4222 | 49.1778 | 50.9333 | 52.6889 | 54.4444 | 56.6889 | 58.9333 | 61.1778 | 63.4222 | 65.6667 | 68.0444 | 70.4222 | 72.8 | 75.1778 | 77.5556 | 80.6 | 83.6444 | 86.6889 | 89.7333 | 92.7778 | 96.1111 | 99.4444 | 102.7778 | 106.1111 | 109.4444
3 | 0.4 | 3004 | 38.2222 | 39.7111 | 41.2 | 42.6889 | 44.1778 | 45.6667 | 47.4222 | 49.1778 | 50.9333 | 52.6889 | 54.4444 | 56.6889 | 58.9333 | 61.1778 | 63.4222 | 65.6667 | 68.0444 | 70.4222 | 72.8 | 75.1778 | 77.5556 | 80.6 | 83.6444 | 86.6889 | 89.7333 | 92.7778 | 96.1111 | 99.4444 | 102.7778 | 106.1111 | 109.4444
3 | 0.6 | 3006 | 39.2222 | 40.8 | 42.3778 | 43.9556 | 45.5333 | 47.1111 | 48.9778 | 50.8444 | 52.7111 | 54.5778 | 56.4444 | 58.6 | 60.7556 | 62.9111 | 65.0667 | 67.2222 | 69.7778 | 72.3333 | 74.8889 | 77.4444 | 80 | 83.1333 | 86.2667 | 89.4 | 92.5333 | 95.6667 | 99.4 | 103.1333 | 106.8667 | 110.6 | 114.3333
3 | 0.8 | 3008 | 40.2222 | 41.8 | 43.3778 | 44.9556 | 46.5333 | 48.1111 | 49.9778 | 51.8444 | 53.7111 | 55.5778 | 57.4444 | 59.6889 | 61.9333 | 64.1778 | 66.4222 | 68.6667 | 71.4222 | 74.1778 | 76.9333 | 79.6889 | 82.4444 | 85.7778 | 89.1111 | 92.4444 | 95.7778 | 99.1111 | 102.9333 | 106.7556 | 110.5778 | 114.4 | 118.2222
3 | 1 | 3010 | 41.2222 | 42.8889 | 44.5556 | 46.2222 | 47.8889 | 49.5556 | 51.4222 | 53.2889 | 55.1556 | 57.0222 | 58.8889 | 61.2444 | 63.6 | 65.9556 | 68.3111 | 70.6667 | 73.5111 | 76.3556 | 79.2 | 82.0444 | 84.8889 | 88.4222 | 91.9556 | 95.4889 | 99.0222 | 102.5556 | 106.5778 | 110.6 | 114.6222 | 118.6444 | 122.6667
3 | 1.2 | 3012 | 42.6667 | 44.1333 | 45.6 | 47.0667 | 48.5333 | 50 | 52.0667 | 54.1333 | 56.2 | 58.2667 | 60.3333 | 62.6889 | 65.0444 | 67.4 | 69.7556 | 72.1111 | 75.1556 | 78.2 | 81.2444 | 84.2889 | 87.3333 | 90.8667 | 94.4 | 97.9333 | 101.4667 | 105 | 109.2222 | 113.4444 | 117.6667 | 121.8889 | 126.1111
3 | 1.4 | 3014 | 43.1111 | 44.6889 | 46.2667 | 47.8444 | 49.4222 | 51 | 53.1556 | 55.3111 | 57.4667 | 59.6222 | 61.7778 | 64.2222 | 66.6667 | 69.1111 | 71.5556 | 74 | 77.1556 | 80.3111 | 83.4667 | 86.6222 | 89.7778 | 93.4 | 97.0222 | 100.6444 | 104.2667 | 107.8889 | 112.3111 | 116.7333 | 121.1556 | 125.5778 | 130
3 | 1.6 | 3016 | 43.6667 | 45.4222 | 47.1778 | 48.9333 | 50.6889 | 52.4444 | 54.5111 | 56.5778 | 58.6444 | 60.7111 | 62.7778 | 65.4222 | 68.0667 | 70.7111 | 73.3556 | 76 | 79.1333 | 82.2667 | 85.4 | 88.5333 | 91.6667 | 95.5111 | 99.3556 | 103.2 | 107.0444 | 110.8889 | 115.2889 | 119.6889 | 124.0889 | 128.4889 | 132.8889
3 | 1.8 | 3018 | 45.1111 | 46.7778 | 48.4444 | 50.1111 | 51.7778 | 53.4444 | 55.6 | 57.7556 | 59.9111 | 62.0667 | 64.2222 | 66.8667 | 69.5111 | 72.1556 | 74.8 | 77.4444 | 80.7778 | 84.1111 | 87.4444 | 90.7778 | 94.1111 | 98.0444 | 101.9778 | 105.9111 | 109.8444 | 113.7778 | 118.2889 | 122.8 | 127.3111 | 131.8222 | 136.3333
3 | 2 | 3020 | 46.1111 | 47.8667 | 49.6222 | 51.3778 | 53.1333 | 54.8889 | 57.0444 | 59.2 | 61.3556 | 63.5111 | 65.6667 | 68.4222 | 71.1778 | 73.9333 | 76.6889 | 79.4444 | 82.7778 | 86.1111 | 89.4444 | 92.7778 | 96.1111 | 100.1333 | 104.1556 | 108.1778 | 112.2 | 116.2222 | 120.9333 | 125.6444 | 130.3556 | 135.0667 | 139.7778
3 | 2.2 | 3022 | 46.5556 | 48.4222 | 50.2889 | 52.1556 | 54.0222 | 55.8889 | 58.1333 | 60.3778 | 62.6222 | 64.8667 | 67.1111 | 70.0444 | 72.9778 | 75.9111 | 78.8444 | 81.7778 | 85.1333 | 88.4889 | 91.8444 | 95.2 | 98.5556 | 102.5778 | 106.6 | 110.6222 | 114.6444 | 118.6667 | 123.3778 | 128.0889 | 132.8 | 137.5111 | 142.2222
3 | 2.4 | 3024 | 47.5556 | 49.4222 | 51.2889 | 53.1556 | 55.0222 | 56.8889 | 59.1333 | 61.3778 | 63.6222 | 65.8667 | 68.1111 | 71.0667 | 74.0222 | 76.9778 | 79.9333 | 82.8889 | 86.3111 | 89.7333 | 93.1556 | 96.5778 | 100 | 104.2222 | 108.4444 | 112.6667 | 116.8889 | 121.1111 | 126.0222 | 130.9333 | 135.8444 | 140.7556 | 145.6667
3 | 2.6 | 3026 | 48.5556 | 50.5111 | 52.4667 | 54.4222 | 56.3778 | 58.3333 | 60.5778 | 62.8222 | 65.0667 | 67.3111 | 69.5556 | 72.5111 | 75.4667 | 78.4222 | 81.3778 | 84.3333 | 87.9556 | 91.5778 | 95.2 | 98.8222 | 102.4444 | 106.6667 | 110.8889 | 115.1111 | 119.3333 | 123.5556 | 128.5556 | 133.5556 | 138.5556 | 143.5556 | 148.5556
3 | 2.8 | 3028 | 49 | 50.9556 | 52.9111 | 54.8667 | 56.8222 | 58.7778 | 61.2222 | 63.6667 | 66.1111 | 68.5556 | 71 | 73.9556 | 76.9111 | 79.8667 | 82.8222 | 85.7778 | 89.5111 | 93.2444 | 96.9778 | 100.7111 | 104.4444 | 108.7556 | 113.0667 | 117.3778 | 121.6889 | 126 | 131 | 136 | 141 | 146 | 151
3 | 3 | 3030 | 50 | 51.9556 | 53.9111 | 55.8667 | 57.8222 | 59.7778 | 62.3333 | 64.8889 | 67.4444 | 70 | 72.5556 | 75.6 | 78.6444 | 81.6889 | 84.7333 | 87.7778 | 91.4 | 95.0222 | 98.6444 | 102.2667 | 105.8889 | 110.3111 | 114.7333 | 119.1556 | 123.5778 | 128 | 133.2 | 138.4 | 143.6 | 148.8 | 154
4 | 0 | 4000 | 35.1111 | 36.5556 | 38 | 39.4444 | 40.8889 | 42.3333 | 43.9111 | 45.4889 | 47.0667 | 48.6444 | 50.2222 | 52.2444 | 54.2667 | 56.2889 | 58.3111 | 60.3333 | 62.6222 | 64.9111 | 67.2 | 69.4889 | 71.7778 | 74.6 | 77.4222 | 80.2444 | 83.0667 | 85.8889 | 88.9556 | 92.0222 | 95.0889 | 98.1556 | 101.2222
4 | 0.4 | 4004 | 35.1111 | 36.5556 | 38 | 39.4444 | 40.8889 | 42.3333 | 43.9111 | 45.4889 | 47.0667 | 48.6444 | 50.2222 | 52.2444 | 54.2667 | 56.2889 | 58.3111 | 60.3333 | 62.6222 | 64.9111 | 67.2 | 69.4889 | 71.7778 | 74.6 | 77.4222 | 80.2444 | 83.0667 | 85.8889 | 88.9556 | 92.0222 | 95.0889 | 98.1556 | 101.2222
4 | 0.6 | 4006 | 36.1111 | 37.6 | 39.0889 | 40.5778 | 42.0667 | 43.5556 | 45.2889 | 47.0222 | 48.7556 | 50.4889 | 52.2222 | 54.2 | 56.1778 | 58.1556 | 60.1333 | 62.1111 | 64.4889 | 66.8667 | 69.2444 | 71.6222 | 74 | 76.8667 | 79.7333 | 82.6 | 85.4667 | 88.3333 | 91.8 | 95.2667 | 98.7333 | 102.2 | 105.6667
4 | 0.8 | 4008 | 37.1111 | 38.6 | 40.0889 | 41.5778 | 43.0667 | 44.5556 | 46.2889 | 48.0222 | 49.7556 | 51.4889 | 53.2222 | 55.2444 | 57.2667 | 59.2889 | 61.3111 | 63.3333 | 65.9111 | 68.4889 | 71.0667 | 73.6444 | 76.2222 | 79.2889 | 82.3556 | 85.4222 | 88.4889 | 91.5556 | 95.0667 | 98.5778 | 102.0889 | 105.6 | 109.1111
4 | 1 | 4010 | 38.1111 | 39.6444 | 41.1778 | 42.7111 | 44.2444 | 45.7778 | 47.5111 | 49.2444 | 50.9778 | 52.7111 | 54.4444 | 56.6222 | 58.8 | 60.9778 | 63.1556 | 65.3333 | 67.9556 | 70.5778 | 73.2 | 75.8222 | 78.4444 | 81.7111 | 84.9778 | 88.2444 | 91.5111 | 94.7778 | 98.4889 | 102.2 | 105.9111 | 109.6222 | 113.3333
4 | 1.2 | 4012 | 39.3333 | 40.6667 | 42 | 43.3333 | 44.6667 | 46 | 47.9333 | 49.8667 | 51.8 | 53.7333 | 55.6667 | 57.8444 | 60.0222 | 62.2 | 64.3778 | 66.5556 | 69.3778 | 72.2 | 75.0222 | 77.8444 | 80.6667 | 83.9333 | 87.2 | 90.4667 | 93.7333 | 97 | 100.9111 | 104.8222 | 108.7333 | 112.6444 | 116.5556
4 | 1.4 | 4014 | 39.5556 | 41.0444 | 42.5333 | 44.0222 | 45.5111 | 47 | 48.9778 | 50.9556 | 52.9333 | 54.9111 | 56.8889 | 59.1111 | 61.3333 | 63.5556 | 65.7778 | 68 | 70.9778 | 73.9556 | 76.9333 | 79.9111 | 82.8889 | 86.2 | 89.5111 | 92.8222 | 96.1333 | 99.4444 | 103.5556 | 107.6667 | 111.7778 | 115.8889 | 120
4 | 1.6 | 4016 | 40.3333 | 41.9111 | 43.4889 | 45.0667 | 46.6444 | 48.2222 | 50.1556 | 52.0889 | 54.0222 | 55.9556 | 57.8889 | 60.3111 | 62.7333 | 65.1556 | 67.5778 | 70 | 72.8667 | 75.7333 | 78.6 | 81.4667 | 84.3333 | 87.9556 | 91.5778 | 95.2 | 98.8222 | 102.4444 | 106.4444 | 110.4444 | 114.4444 | 118.4444 | 122.4444
4 | 1.8 | 4018 | 41.5556 | 43.0889 | 44.6222 | 46.1556 | 47.6889 | 49.2222 | 51.2 | 53.1778 | 55.1556 | 57.1333 | 59.1111 | 61.5333 | 63.9556 | 66.3778 | 68.8 | 71.2222 | 74.2889 | 77.3556 | 80.4222 | 83.4889 | 86.5556 | 90.2222 | 93.8889 | 97.5556 | 101.2222 | 104.8889 | 109.0444 | 113.2 | 117.3556 | 121.5111 | 125.6667
4 | 2 | 4020 | 42.5556 | 44.1333 | 45.7111 | 47.2889 | 48.8667 | 50.4444 | 52.4222 | 54.4 | 56.3778 | 58.3556 | 60.3333 | 62.9111 | 65.4889 | 68.0667 | 70.6444 | 73.2222 | 76.2889 | 79.3556 | 82.4222 | 85.4889 | 88.5556 | 92.2667 | 95.9778 | 99.6889 | 103.4 | 107.1111 | 111.4667 | 115.8222 | 120.1778 | 124.5333 | 128.8889
4 | 2.2 | 4022 | 42.7778 | 44.5111 | 46.2444 | 47.9778 | 49.7111 | 51.4444 | 53.4667 | 55.4889 | 57.5111 | 59.5333 | 61.5556 | 64.2222 | 66.8889 | 69.5556 | 72.2222 | 74.8889 | 78.0667 | 81.2444 | 84.4222 | 87.6 | 90.7778 | 94.4889 | 98.2 | 101.9111 | 105.6222 | 109.3333 | 113.6889 | 118.0444 | 122.4 | 126.7556 | 131.1111
4 | 2.4 | 4024 | 43.7778 | 45.5111 | 47.2444 | 48.9778 | 50.7111 | 52.4444 | 54.4667 | 56.4889 | 58.5111 | 60.5333 | 62.5556 | 65.3333 | 68.1111 | 70.8889 | 73.6667 | 76.4444 | 79.5556 | 82.6667 | 85.7778 | 88.8889 | 92 | 95.9111 | 99.8222 | 103.7333 | 107.6444 | 111.5556 | 116.1111 | 120.6667 | 125.2222 | 129.7778 | 134.3333
4 | 2.6 | 4026 | 44.7778 | 46.5556 | 48.3333 | 50.1111 | 51.8889 | 53.6667 | 55.6889 | 57.7111 | 59.7333 | 61.7556 | 63.7778 | 66.5556 | 69.3333 | 72.1111 | 74.8889 | 77.6667 | 80.9778 | 84.2889 | 87.6 | 90.9111 | 94.2222 | 98.1333 | 102.0444 | 105.9556 | 109.8667 | 113.7778 | 118.3778 | 122.9778 | 127.5778 | 132.1778 | 136.7778
4 | 2.8 | 4028 | 45 | 46.7778 | 48.5556 | 50.3333 | 52.1111 | 53.8889 | 56.1111 | 58.3333 | 60.5556 | 62.7778 | 65 | 67.7778 | 70.5556 | 73.3333 | 76.1111 | 78.8889 | 82.3556 | 85.8222 | 89.2889 | 92.7556 | 96.2222 | 100.1778 | 104.1333 | 108.0889 | 112.0444 | 116 | 120.6 | 125.2 | 129.8 | 134.4 | 139
4 | 3 | 4030 | 46 | 47.7778 | 49.5556 | 51.3333 | 53.1111 | 54.8889 | 57.2667 | 59.6444 | 62.0222 | 64.4 | 66.7778 | 69.6 | 72.4222 | 75.2444 | 78.0667 | 80.8889 | 84.2 | 87.5111 | 90.8222 | 94.1333 | 97.4444 | 101.5556 | 105.6667 | 109.7778 | 113.8889 | 118 | 122.8 | 127.6 | 132.4 | 137.2 | 142
5 | 0 | 5000 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 81.8 | 84.6 | 87.4 | 90.2 | 93
5 | 0.4 | 5004 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 81.8 | 84.6 | 87.4 | 90.2 | 93
5 | 0.6 | 5006 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.6 | 73.2 | 75.8 | 78.4 | 81 | 84.2 | 87.4 | 90.6 | 93.8 | 97
5 | 0.8 | 5008 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 50.8 | 52.6 | 54.4 | 56.2 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.2 | 90.4 | 93.6 | 96.8 | 100
5 | 1 | 5010 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 52 | 54 | 56 | 58 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 75 | 78 | 81 | 84 | 87 | 90.4 | 93.8 | 97.2 | 100.6 | 104
5 | 1.2 | 5012 | 36 | 37.2 | 38.4 | 39.6 | 40.8 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53 | 55 | 57 | 59 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.6 | 96.2 | 99.8 | 103.4 | 107
5 | 1.4 | 5014 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54 | 56 | 58 | 60 | 62 | 64.8 | 67.6 | 70.4 | 73.2 | 76 | 79 | 82 | 85 | 88 | 91 | 94.8 | 98.6 | 102.4 | 106.2 | 110
5 | 1.6 | 5016 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 80.4 | 83.8 | 87.2 | 90.6 | 94 | 97.6 | 101.2 | 104.8 | 108.4 | 112
5 | 1.8 | 5018 | 38 | 39.4 | 40.8 | 42.2 | 43.6 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 82.4 | 85.8 | 89.2 | 92.6 | 96 | 99.8 | 103.6 | 107.4 | 111.2 | 115
5 | 2 | 5020 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.4 | 87.8 | 91.2 | 94.6 | 98 | 102 | 106 | 110 | 114 | 118
5 | 2.2 | 5022 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56 | 58.4 | 60.8 | 63.2 | 65.6 | 68 | 71 | 74 | 77 | 80 | 83 | 86.4 | 89.8 | 93.2 | 96.6 | 100 | 104 | 108 | 112 | 116 | 120
5 | 2.4 | 5024 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.6 | 62.2 | 64.8 | 67.4 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.6 | 91.2 | 94.8 | 98.4 | 102 | 106.2 | 110.4 | 114.6 | 118.8 | 123
5 | 2.6 | 5026 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 50.8 | 52.6 | 54.4 | 56.2 | 58 | 60.6 | 63.2 | 65.8 | 68.4 | 71 | 74 | 77 | 80 | 83 | 86 | 89.6 | 93.2 | 96.8 | 100.4 | 104 | 108.2 | 112.4 | 116.6 | 120.8 | 125
5 | 2.8 | 5028 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51 | 53 | 55 | 57 | 59 | 61.6 | 64.2 | 66.8 | 69.4 | 72 | 75.2 | 78.4 | 81.6 | 84.8 | 88 | 91.6 | 95.2 | 98.8 | 102.4 | 106 | 110.2 | 114.4 | 118.6 | 122.8 | 127
5 | 3 | 5030 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 52.2 | 54.4 | 56.6 | 58.8 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.8 | 96.6 | 100.4 | 104.2 | 108 | 112.4 | 116.8 | 121.2 | 125.6 | 130
6 | 0 | 6000 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.52 | 47.24 | 48.96 | 50.68 | 52.4 | 54.48 | 56.56 | 58.64 | 60.72 | 62.8 | 65.24 | 67.68 | 70.12 | 72.56 | 75 | 77.68 | 80.36 | 83.04 | 85.72 | 88.4
6 | 0.4 | 6004 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.52 | 47.24 | 48.96 | 50.68 | 52.4 | 54.48 | 56.56 | 58.64 | 60.72 | 62.8 | 65.24 | 67.68 | 70.12 | 72.56 | 75 | 77.68 | 80.36 | 83.04 | 85.72 | 88.4
6 | 0.6 | 6006 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.32 | 49.04 | 50.76 | 52.48 | 54.2 | 56.28 | 58.36 | 60.44 | 62.52 | 64.6 | 67.08 | 69.56 | 72.04 | 74.52 | 77 | 80.04 | 83.08 | 86.12 | 89.16 | 92.2
6 | 0.8 | 6008 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.32 | 50.04 | 51.76 | 53.48 | 55.2 | 57.48 | 59.76 | 62.04 | 64.32 | 66.6 | 69.24 | 71.88 | 74.52 | 77.16 | 79.8 | 82.84 | 85.88 | 88.92 | 91.96 | 95
6 | 1 | 6010 | 33.2 | 34.52 | 35.84 | 37.16 | 38.48 | 39.8 | 41.32 | 42.84 | 44.36 | 45.88 | 47.4 | 49.32 | 51.24 | 53.16 | 55.08 | 57 | 59.28 | 61.56 | 63.84 | 66.12 | 68.4 | 71.24 | 74.08 | 76.92 | 79.76 | 82.6 | 85.84 | 89.08 | 92.32 | 95.56 | 98.8
6 | 1.2 | 6012 | 34.2 | 35.36 | 36.52 | 37.68 | 38.84 | 40 | 41.68 | 43.36 | 45.04 | 46.72 | 48.4 | 50.32 | 52.24 | 54.16 | 56.08 | 58 | 60.44 | 62.88 | 65.32 | 67.76 | 70.2 | 73.08 | 75.96 | 78.84 | 81.72 | 84.6 | 88 | 91.4 | 94.8 | 98.2 | 101.6
6 | 1.4 | 6014 | 34.2 | 35.56 | 36.92 | 38.28 | 39.64 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4 | 51.32 | 53.24 | 55.16 | 57.08 | 59 | 61.64 | 64.28 | 66.92 | 69.56 | 72.2 | 75.08 | 77.96 | 80.84 | 83.72 | 86.6 | 90.16 | 93.72 | 97.28 | 100.84 | 104.4
6 | 1.6 | 6016 | 35.2 | 36.52 | 37.84 | 39.16 | 40.48 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8 | 63.28 | 65.76 | 68.24 | 70.72 | 73.2 | 76.4 | 79.6 | 82.8 | 86 | 89.2 | 92.64 | 96.08 | 99.52 | 102.96 | 106.4
6 | 1.8 | 6018 | 36.2 | 37.52 | 38.84 | 40.16 | 41.48 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.48 | 55.56 | 57.64 | 59.72 | 61.8 | 64.48 | 67.16 | 69.84 | 72.52 | 75.2 | 78.4 | 81.6 | 84.8 | 88 | 91.2 | 94.8 | 98.4 | 102 | 105.6 | 109.2
6 | 2 | 6020 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.48 | 47.16 | 48.84 | 50.52 | 52.2 | 54.48 | 56.76 | 59.04 | 61.32 | 63.6 | 66.28 | 68.96 | 71.64 | 74.32 | 77 | 80.24 | 83.48 | 86.72 | 89.96 | 93.2 | 96.96 | 100.72 | 104.48 | 108.24 | 112
6 | 2.2 | 6022 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.48 | 57.76 | 60.04 | 62.32 | 64.6 | 67.44 | 70.28 | 73.12 | 75.96 | 78.8 | 82.04 | 85.28 | 88.52 | 91.76 | 95 | 98.8 | 102.6 | 106.4 | 110.2 | 114
6 | 2.4 | 6024 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.32 | 49.04 | 50.76 | 52.48 | 54.2 | 56.64 | 59.08 | 61.52 | 63.96 | 66.4 | 69.08 | 71.76 | 74.44 | 77.12 | 79.8 | 83.24 | 86.68 | 90.12 | 93.56 | 97 | 100.96 | 104.92 | 108.88 | 112.84 | 116.8
6 | 2.6 | 6026 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.32 | 50.04 | 51.76 | 53.48 | 55.2 | 57.64 | 60.08 | 62.52 | 64.96 | 67.4 | 70.28 | 73.16 | 76.04 | 78.92 | 81.8 | 85.2 | 88.6 | 92 | 95.4 | 98.8 | 102.8 | 106.8 | 110.8 | 114.8 | 118.8
6 | 2.8 | 6028 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.52 | 50.44 | 52.36 | 54.28 | 56.2 | 58.64 | 61.08 | 63.52 | 65.96 | 68.4 | 71.44 | 74.48 | 77.52 | 80.56 | 83.6 | 87.04 | 90.48 | 93.92 | 97.36 | 100.8 | 104.8 | 108.8 | 112.8 | 116.8 | 120.8
6 | 3 | 6030 | 40 | 41.52 | 43.04 | 44.56 | 46.08 | 47.6 | 49.68 | 51.76 | 53.84 | 55.92 | 58 | 60.44 | 62.88 | 65.32 | 67.76 | 70.2 | 73.08 | 75.96 | 78.84 | 81.72 | 84.6 | 88.2 | 91.8 | 95.4 | 99 | 102.6 | 106.76 | 110.92 | 115.08 | 119.24 | 123.4
7 | 0 | 7000 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.24 | 44.88 | 46.52 | 48.16 | 49.8 | 51.76 | 53.72 | 55.68 | 57.64 | 59.6 | 61.88 | 64.16 | 66.44 | 68.72 | 71 | 73.56 | 76.12 | 78.68 | 81.24 | 83.8
7 | 0.4 | 7004 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.24 | 44.88 | 46.52 | 48.16 | 49.8 | 51.76 | 53.72 | 55.68 | 57.64 | 59.6 | 61.88 | 64.16 | 66.44 | 68.72 | 71 | 73.56 | 76.12 | 78.68 | 81.24 | 83.8
7 | 0.6 | 7006 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.84 | 46.48 | 48.12 | 49.76 | 51.4 | 53.36 | 55.32 | 57.28 | 59.24 | 61.2 | 63.56 | 65.92 | 68.28 | 70.64 | 73 | 75.88 | 78.76 | 81.64 | 84.52 | 87.4
7 | 0.8 | 7008 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.84 | 47.48 | 49.12 | 50.76 | 52.4 | 54.56 | 56.72 | 58.88 | 61.04 | 63.2 | 65.68 | 68.16 | 70.64 | 73.12 | 75.6 | 78.48 | 81.36 | 84.24 | 87.12 | 90
7 | 1 | 7010 | 31.4 | 32.64 | 33.88 | 35.12 | 36.36 | 37.6 | 39.04 | 40.48 | 41.92 | 43.36 | 44.8 | 46.64 | 48.48 | 50.32 | 52.16 | 54 | 56.16 | 58.32 | 60.48 | 62.64 | 64.8 | 67.48 | 70.16 | 72.84 | 75.52 | 78.2 | 81.28 | 84.36 | 87.44 | 90.52 | 93.6
7 | 1.2 | 7012 | 32.4 | 33.52 | 34.64 | 35.76 | 36.88 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.64 | 49.48 | 51.32 | 53.16 | 55 | 57.28 | 59.56 | 61.84 | 64.12 | 66.4 | 69.16 | 71.92 | 74.68 | 77.44 | 80.2 | 83.4 | 86.6 | 89.8 | 93 | 96.2
7 | 1.4 | 7014 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.64 | 50.48 | 52.32 | 54.16 | 56 | 58.48 | 60.96 | 63.44 | 65.92 | 68.4 | 71.16 | 73.92 | 76.68 | 79.44 | 82.2 | 85.52 | 88.84 | 92.16 | 95.48 | 98.8
7 | 1.6 | 7016 | 33.4 | 34.64 | 35.88 | 37.12 | 38.36 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6 | 59.96 | 62.32 | 64.68 | 67.04 | 69.4 | 72.4 | 75.4 | 78.4 | 81.4 | 84.4 | 87.68 | 90.96 | 94.24 | 97.52 | 100.8
7 | 1.8 | 7018 | 34.4 | 35.64 | 36.88 | 38.12 | 39.36 | 40.6 | 42.24 | 43.88 | 45.52 | 47.16 | 48.8 | 50.76 | 52.72 | 54.68 | 56.64 | 58.6 | 61.16 | 63.72 | 66.28 | 68.84 | 71.4 | 74.4 | 77.4 | 80.4 | 83.4 | 86.4 | 89.8 | 93.2 | 96.6 | 100 | 103.4
7 | 2 | 7020 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.16 | 44.72 | 46.28 | 47.84 | 49.4 | 51.56 | 53.72 | 55.88 | 58.04 | 60.2 | 62.76 | 65.32 | 67.88 | 70.44 | 73 | 76.08 | 79.16 | 82.24 | 85.32 | 88.4 | 91.92 | 95.44 | 98.96 | 102.48 | 106
7 | 2.2 | 7022 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4 | 52.56 | 54.72 | 56.88 | 59.04 | 61.2 | 63.88 | 66.56 | 69.24 | 71.92 | 74.6 | 77.68 | 80.76 | 83.84 | 86.92 | 90 | 93.6 | 97.2 | 100.8 | 104.4 | 108
7 | 2.4 | 7024 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.84 | 46.48 | 48.12 | 49.76 | 51.4 | 53.68 | 55.96 | 58.24 | 60.52 | 62.8 | 65.36 | 67.92 | 70.48 | 73.04 | 75.6 | 78.88 | 82.16 | 85.44 | 88.72 | 92 | 95.72 | 99.44 | 103.16 | 106.88 | 110.6
7 | 2.6 | 7026 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.84 | 47.48 | 49.12 | 50.76 | 52.4 | 54.68 | 56.96 | 59.24 | 61.52 | 63.8 | 66.56 | 69.32 | 72.08 | 74.84 | 77.6 | 80.8 | 84 | 87.2 | 90.4 | 93.6 | 97.4 | 101.2 | 105 | 108.8 | 112.6
7 | 2.8 | 7028 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 46.04 | 47.88 | 49.72 | 51.56 | 53.4 | 55.68 | 57.96 | 60.24 | 62.52 | 64.8 | 67.68 | 70.56 | 73.44 | 76.32 | 79.2 | 82.48 | 85.76 | 89.04 | 92.32 | 95.6 | 99.4 | 103.2 | 107 | 110.8 | 114.6
7 | 3 | 7030 | 38 | 39.44 | 40.88 | 42.32 | 43.76 | 45.2 | 47.16 | 49.12 | 51.08 | 53.04 | 55 | 57.28 | 59.56 | 61.84 | 64.12 | 66.4 | 69.16 | 71.92 | 74.68 | 77.44 | 80.2 | 83.6 | 87 | 90.4 | 93.8 | 97.2 | 101.12 | 105.04 | 108.96 | 112.88 | 116.8
8 | 0 | 8000 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.96 | 42.52 | 44.08 | 45.64 | 47.2 | 49.04 | 50.88 | 52.72 | 54.56 | 56.4 | 58.52 | 60.64 | 62.76 | 64.88 | 67 | 69.44 | 71.88 | 74.32 | 76.76 | 79.2
8 | 0.4 | 8004 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.96 | 42.52 | 44.08 | 45.64 | 47.2 | 49.04 | 50.88 | 52.72 | 54.56 | 56.4 | 58.52 | 60.64 | 62.76 | 64.88 | 67 | 69.44 | 71.88 | 74.32 | 76.76 | 79.2
8 | 0.6 | 8006 | 28.2 | 29.36 | 30.52 | 31.68 | 32.84 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.36 | 43.92 | 45.48 | 47.04 | 48.6 | 50.44 | 52.28 | 54.12 | 55.96 | 57.8 | 60.04 | 62.28 | 64.52 | 66.76 | 69 | 71.72 | 74.44 | 77.16 | 79.88 | 82.6
8 | 0.8 | 8008 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.36 | 44.92 | 46.48 | 48.04 | 49.6 | 51.64 | 53.68 | 55.72 | 57.76 | 59.8 | 62.12 | 64.44 | 66.76 | 69.08 | 71.4 | 74.12 | 76.84 | 79.56 | 82.28 | 85
8 | 1 | 8010 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2 | 43.96 | 45.72 | 47.48 | 49.24 | 51 | 53.04 | 55.08 | 57.12 | 59.16 | 61.2 | 63.72 | 66.24 | 68.76 | 71.28 | 73.8 | 76.72 | 79.64 | 82.56 | 85.48 | 88.4
8 | 1.2 | 8012 | 30.6 | 31.68 | 32.76 | 33.84 | 34.92 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52 | 54.12 | 56.24 | 58.36 | 60.48 | 62.6 | 65.24 | 67.88 | 70.52 | 73.16 | 75.8 | 78.8 | 81.8 | 84.8 | 87.8 | 90.8
8 | 1.4 | 8014 | 30.6 | 31.88 | 33.16 | 34.44 | 35.72 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53 | 55.32 | 57.64 | 59.96 | 62.28 | 64.6 | 67.24 | 69.88 | 72.52 | 75.16 | 77.8 | 80.88 | 83.96 | 87.04 | 90.12 | 93.2
8 | 1.6 | 8016 | 31.6 | 32.76 | 33.92 | 35.08 | 36.24 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.04 | 48.88 | 50.72 | 52.56 | 54.4 | 56.64 | 58.88 | 61.12 | 63.36 | 65.6 | 68.4 | 71.2 | 74 | 76.8 | 79.6 | 82.72 | 85.84 | 88.96 | 92.08 | 95.2
8 | 1.8 | 8018 | 32.6 | 33.76 | 34.92 | 36.08 | 37.24 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.04 | 49.88 | 51.72 | 53.56 | 55.4 | 57.84 | 60.28 | 62.72 | 65.16 | 67.6 | 70.4 | 73.2 | 76 | 78.8 | 81.6 | 84.8 | 88 | 91.2 | 94.4 | 97.6
8 | 2 | 8020 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.84 | 42.28 | 43.72 | 45.16 | 46.6 | 48.64 | 50.68 | 52.72 | 54.76 | 56.8 | 59.24 | 61.68 | 64.12 | 66.56 | 69 | 71.92 | 74.84 | 77.76 | 80.68 | 83.6 | 86.88 | 90.16 | 93.44 | 96.72 | 100
8 | 2.2 | 8022 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.36 | 42.92 | 44.48 | 46.04 | 47.6 | 49.64 | 51.68 | 53.72 | 55.76 | 57.8 | 60.32 | 62.84 | 65.36 | 67.88 | 70.4 | 73.32 | 76.24 | 79.16 | 82.08 | 85 | 88.4 | 91.8 | 95.2 | 98.6 | 102
8 | 2.4 | 8024 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.36 | 43.92 | 45.48 | 47.04 | 48.6 | 50.72 | 52.84 | 54.96 | 57.08 | 59.2 | 61.64 | 64.08 | 66.52 | 68.96 | 71.4 | 74.52 | 77.64 | 80.76 | 83.88 | 87 | 90.48 | 93.96 | 97.44 | 100.92 | 104.4
8 | 2.6 | 8026 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.36 | 44.92 | 46.48 | 48.04 | 49.6 | 51.72 | 53.84 | 55.96 | 58.08 | 60.2 | 62.84 | 65.48 | 68.12 | 70.76 | 73.4 | 76.4 | 79.4 | 82.4 | 85.4 | 88.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4
8 | 2.8 | 8028 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.56 | 45.32 | 47.08 | 48.84 | 50.6 | 52.72 | 54.84 | 56.96 | 59.08 | 61.2 | 63.92 | 66.64 | 69.36 | 72.08 | 74.8 | 77.92 | 81.04 | 84.16 | 87.28 | 90.4 | 94 | 97.6 | 101.2 | 104.8 | 108.4
8 | 3 | 8030 | 36 | 37.36 | 38.72 | 40.08 | 41.44 | 42.8 | 44.64 | 46.48 | 48.32 | 50.16 | 52 | 54.12 | 56.24 | 58.36 | 60.48 | 62.6 | 65.24 | 67.88 | 70.52 | 73.16 | 75.8 | 79 | 82.2 | 85.4 | 88.6 | 91.8 | 95.48 | 99.16 | 102.84 | 106.52 | 110.2
9 | 0 | 9000 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.16 | 57.12 | 59.08 | 61.04 | 63 | 65.32 | 67.64 | 69.96 | 72.28 | 74.6
9 | 0.4 | 9004 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.16 | 57.12 | 59.08 | 61.04 | 63 | 65.32 | 67.64 | 69.96 | 72.28 | 74.6
9 | 0.6 | 9006 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.88 | 41.36 | 42.84 | 44.32 | 45.8 | 47.52 | 49.24 | 50.96 | 52.68 | 54.4 | 56.52 | 58.64 | 60.76 | 62.88 | 65 | 67.56 | 70.12 | 72.68 | 75.24 | 77.8
9 | 0.8 | 9008 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.88 | 42.36 | 43.84 | 45.32 | 46.8 | 48.72 | 50.64 | 52.56 | 54.48 | 56.4 | 58.56 | 60.72 | 62.88 | 65.04 | 67.2 | 69.76 | 72.32 | 74.88 | 77.44 | 80
9 | 1 | 9010 | 27.8 | 28.88 | 29.96 | 31.04 | 32.12 | 33.2 | 34.48 | 35.76 | 37.04 | 38.32 | 39.6 | 41.28 | 42.96 | 44.64 | 46.32 | 48 | 49.92 | 51.84 | 53.76 | 55.68 | 57.6 | 59.96 | 62.32 | 64.68 | 67.04 | 69.4 | 72.16 | 74.92 | 77.68 | 80.44 | 83.2
9 | 1.2 | 9012 | 28.8 | 29.84 | 30.88 | 31.92 | 32.96 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.28 | 43.96 | 45.64 | 47.32 | 49 | 50.96 | 52.92 | 54.88 | 56.84 | 58.8 | 61.32 | 63.84 | 66.36 | 68.88 | 71.4 | 74.2 | 77 | 79.8 | 82.6 | 85.4
9 | 1.4 | 9014 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.28 | 44.96 | 46.64 | 48.32 | 50 | 52.16 | 54.32 | 56.48 | 58.64 | 60.8 | 63.32 | 65.84 | 68.36 | 70.88 | 73.4 | 76.24 | 79.08 | 81.92 | 84.76 | 87.6
9 | 1.6 | 9016 | 29.8 | 30.88 | 31.96 | 33.04 | 34.12 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.32 | 46.04 | 47.76 | 49.48 | 51.2 | 53.32 | 55.44 | 57.56 | 59.68 | 61.8 | 64.4 | 67 | 69.6 | 72.2 | 74.8 | 77.76 | 80.72 | 83.68 | 86.64 | 89.6
9 | 1.8 | 9018 | 30.8 | 31.88 | 32.96 | 34.04 | 35.12 | 36.2 | 37.68 | 39.16 | 40.64 | 42.12 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2 | 54.52 | 56.84 | 59.16 | 61.48 | 63.8 | 66.4 | 69 | 71.6 | 74.2 | 76.8 | 79.8 | 82.8 | 85.8 | 88.8 | 91.8
9 | 2 | 9020 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.52 | 39.84 | 41.16 | 42.48 | 43.8 | 45.72 | 47.64 | 49.56 | 51.48 | 53.4 | 55.72 | 58.04 | 60.36 | 62.68 | 65 | 67.76 | 70.52 | 73.28 | 76.04 | 78.8 | 81.84 | 84.88 | 87.92 | 90.96 | 94
9 | 2.2 | 9022 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8 | 46.72 | 48.64 | 50.56 | 52.48 | 54.4 | 56.76 | 59.12 | 61.48 | 63.84 | 66.2 | 68.96 | 71.72 | 74.48 | 77.24 | 80 | 83.2 | 86.4 | 89.6 | 92.8 | 96
9 | 2.4 | 9024 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.88 | 41.36 | 42.84 | 44.32 | 45.8 | 47.76 | 49.72 | 51.68 | 53.64 | 55.6 | 57.92 | 60.24 | 62.56 | 64.88 | 67.2 | 70.16 | 73.12 | 76.08 | 79.04 | 82 | 85.24 | 88.48 | 91.72 | 94.96 | 98.2
9 | 2.6 | 9026 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.88 | 42.36 | 43.84 | 45.32 | 46.8 | 48.76 | 50.72 | 52.68 | 54.64 | 56.6 | 59.12 | 61.64 | 64.16 | 66.68 | 69.2 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86.6 | 90 | 93.4 | 96.8 | 100.2
9 | 2.8 | 9028 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 41.08 | 42.76 | 44.44 | 46.12 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6 | 60.16 | 62.72 | 65.28 | 67.84 | 70.4 | 73.36 | 76.32 | 79.28 | 82.24 | 85.2 | 88.6 | 92 | 95.4 | 98.8 | 102.2
9 | 3 | 9030 | 34 | 35.28 | 36.56 | 37.84 | 39.12 | 40.4 | 42.12 | 43.84 | 45.56 | 47.28 | 49 | 50.96 | 52.92 | 54.88 | 56.84 | 58.8 | 61.32 | 63.84 | 66.36 | 68.88 | 71.4 | 74.4 | 77.4 | 80.4 | 83.4 | 86.4 | 89.84 | 93.28 | 96.72 | 100.16 | 103.6
10 | 0 | 10000 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70
10 | 0.4 | 10004 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70
10 | 0.6 | 10006 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.6 | 46.2 | 47.8 | 49.4 | 51 | 53 | 55 | 57 | 59 | 61 | 63.4 | 65.8 | 68.2 | 70.6 | 73
10 | 0.8 | 10008 | 26 | 27 | 28 | 29 | 30 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55 | 57 | 59 | 61 | 63 | 65.4 | 67.8 | 70.2 | 72.6 | 75
10 | 1 | 10010 | 26 | 27 | 28 | 29 | 30 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78
10 | 1.2 | 10012 | 27 | 28 | 29 | 30 | 31 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.6 | 72.2 | 74.8 | 77.4 | 80
10 | 1.4 | 10014 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 49 | 51 | 53 | 55 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.6 | 74.2 | 76.8 | 79.4 | 82
10 | 1.6 | 10016 | 28 | 29 | 30 | 31 | 32 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 50 | 52 | 54 | 56 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84
10 | 1.8 | 10018 | 29 | 30 | 31 | 32 | 33 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51.2 | 53.4 | 55.6 | 57.8 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86
10 | 2 | 10020 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.2 | 37.4 | 38.6 | 39.8 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 52.2 | 54.4 | 56.6 | 58.8 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 76.8 | 79.6 | 82.4 | 85.2 | 88
10 | 2.2 | 10022 | 30 | 31 | 32 | 33 | 34 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53.2 | 55.4 | 57.6 | 59.8 | 62 | 64.6 | 67.2 | 69.8 | 72.4 | 75 | 78 | 81 | 84 | 87 | 90
10 | 2.4 | 10024 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63 | 65.8 | 68.6 | 71.4 | 74.2 | 77 | 80 | 83 | 86 | 89 | 92
10 | 2.6 | 10026 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.4 | 57.8 | 60.2 | 62.6 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78 | 81.2 | 84.4 | 87.6 | 90.8 | 94
10 | 2.8 | 10028 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.4 | 58.8 | 61.2 | 63.6 | 66 | 68.8 | 71.6 | 74.4 | 77.2 | 80 | 83.2 | 86.4 | 89.6 | 92.8 | 96
10 | 3 | 10030 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.2 | 87.4 | 90.6 | 93.8 | 97
11 | 0 | 11000 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.28 | 29.36 | 30.44 | 31.52 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.68 | 42.16 | 43.64 | 45.12 | 46.6 | 48.28 | 49.96 | 51.64 | 53.32 | 55 | 57.08 | 59.16 | 61.24 | 63.32 | 65.4
11 | 0.4 | 11004 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.28 | 29.36 | 30.44 | 31.52 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.68 | 42.16 | 43.64 | 45.12 | 46.6 | 48.28 | 49.96 | 51.64 | 53.32 | 55 | 57.08 | 59.16 | 61.24 | 63.32 | 65.4
11 | 0.6 | 11006 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2 | 41.68 | 43.16 | 44.64 | 46.12 | 47.6 | 49.48 | 51.36 | 53.24 | 55.12 | 57 | 59.24 | 61.48 | 63.72 | 65.96 | 68.2
11 | 0.8 | 11008 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 29.92 | 31.04 | 32.16 | 33.28 | 34.4 | 35.72 | 37.04 | 38.36 | 39.68 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4 | 51.28 | 53.16 | 55.04 | 56.92 | 58.8 | 61.04 | 63.28 | 65.52 | 67.76 | 70
11 | 1 | 11010 | 24.4 | 25.32 | 26.24 | 27.16 | 28.08 | 29 | 30.12 | 31.24 | 32.36 | 33.48 | 34.6 | 36.08 | 37.56 | 39.04 | 40.52 | 42 | 43.68 | 45.36 | 47.04 | 48.72 | 50.4 | 52.44 | 54.48 | 56.52 | 58.56 | 60.6 | 63.04 | 65.48 | 67.92 | 70.36 | 72.8
11 | 1.2 | 11012 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.92 | 38.44 | 39.96 | 41.48 | 43 | 44.68 | 46.36 | 48.04 | 49.72 | 51.4 | 53.64 | 55.88 | 58.12 | 60.36 | 62.6 | 65 | 67.4 | 69.8 | 72.2 | 74.6
11 | 1.4 | 11014 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8 | 45.68 | 47.56 | 49.44 | 51.32 | 53.2 | 55.44 | 57.68 | 59.92 | 62.16 | 64.4 | 66.84 | 69.28 | 71.72 | 74.16 | 76.6
11 | 1.6 | 11016 | 26.2 | 27.12 | 28.04 | 28.96 | 29.88 | 30.8 | 32.08 | 33.36 | 34.64 | 35.92 | 37.2 | 38.72 | 40.24 | 41.76 | 43.28 | 44.8 | 46.68 | 48.56 | 50.44 | 52.32 | 54.2 | 56.44 | 58.68 | 60.92 | 63.16 | 65.4 | 68 | 70.6 | 73.2 | 75.8 | 78.4
11 | 1.8 | 11018 | 27 | 27.96 | 28.92 | 29.88 | 30.84 | 31.8 | 33.08 | 34.36 | 35.64 | 36.92 | 38.2 | 39.72 | 41.24 | 42.76 | 44.28 | 45.8 | 47.84 | 49.88 | 51.92 | 53.96 | 56 | 58.24 | 60.48 | 62.72 | 64.96 | 67.2 | 69.84 | 72.48 | 75.12 | 77.76 | 80.4
11 | 2 | 11020 | 27 | 28.12 | 29.24 | 30.36 | 31.48 | 32.6 | 33.76 | 34.92 | 36.08 | 37.24 | 38.4 | 40.04 | 41.68 | 43.32 | 44.96 | 46.6 | 48.68 | 50.76 | 52.84 | 54.92 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.64 | 74.28 | 76.92 | 79.56 | 82.2
11 | 2.2 | 11022 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.88 | 42.56 | 44.24 | 45.92 | 47.6 | 49.64 | 51.68 | 53.72 | 55.76 | 57.8 | 60.24 | 62.68 | 65.12 | 67.56 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84
11 | 2.4 | 11024 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2 | 41.88 | 43.56 | 45.24 | 46.92 | 48.6 | 50.64 | 52.68 | 54.72 | 56.76 | 58.8 | 61.4 | 64 | 66.6 | 69.2 | 71.8 | 74.6 | 77.4 | 80.2 | 83 | 85.8
11 | 2.6 | 11026 | 28.8 | 29.92 | 31.04 | 32.16 | 33.28 | 34.4 | 35.72 | 37.04 | 38.36 | 39.68 | 41 | 42.72 | 44.44 | 46.16 | 47.88 | 49.6 | 51.8 | 54 | 56.2 | 58.4 | 60.6 | 63.04 | 65.48 | 67.92 | 70.36 | 72.8 | 75.8 | 78.8 | 81.8 | 84.8 | 87.8
11 | 2.8 | 11028 | 29 | 30.12 | 31.24 | 32.36 | 33.48 | 34.6 | 36.08 | 37.56 | 39.04 | 40.52 | 42 | 43.68 | 45.36 | 47.04 | 48.72 | 50.4 | 52.64 | 54.88 | 57.12 | 59.36 | 61.6 | 64.2 | 66.8 | 69.4 | 72 | 74.6 | 77.6 | 80.6 | 83.6 | 86.6 | 89.6
11 | 3 | 11030 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.88 | 38.36 | 39.84 | 41.32 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.64 | 55.88 | 58.12 | 60.36 | 62.6 | 65.2 | 67.8 | 70.4 | 73 | 75.6 | 78.6 | 81.6 | 84.6 | 87.6 | 90.6
12 | 0 | 12000 | 20.8 | 21.72 | 22.64 | 23.56 | 24.48 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.76 | 39.12 | 40.48 | 41.84 | 43.2 | 44.76 | 46.32 | 47.88 | 49.44 | 51 | 52.96 | 54.92 | 56.88 | 58.84 | 60.8
12 | 0.4 | 12004 | 20.8 | 21.72 | 22.64 | 23.56 | 24.48 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.76 | 39.12 | 40.48 | 41.84 | 43.2 | 44.76 | 46.32 | 47.88 | 49.44 | 51 | 52.96 | 54.92 | 56.88 | 58.84 | 60.8
12 | 0.6 | 12006 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 38.76 | 40.12 | 41.48 | 42.84 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53 | 55.08 | 57.16 | 59.24 | 61.32 | 63.4
12 | 0.8 | 12008 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 33.04 | 34.28 | 35.52 | 36.76 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.56 | 49.32 | 51.08 | 52.84 | 54.6 | 56.68 | 58.76 | 60.84 | 62.92 | 65
12 | 1 | 12010 | 22.8 | 23.64 | 24.48 | 25.32 | 26.16 | 27 | 28.04 | 29.08 | 30.12 | 31.16 | 32.2 | 33.56 | 34.92 | 36.28 | 37.64 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.68 | 50.56 | 52.44 | 54.32 | 56.2 | 58.48 | 60.76 | 63.04 | 65.32 | 67.6
12 | 1.2 | 12012 | 23.4 | 24.24 | 25.08 | 25.92 | 26.76 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8 | 34.24 | 35.68 | 37.12 | 38.56 | 40 | 41.56 | 43.12 | 44.68 | 46.24 | 47.8 | 49.88 | 51.96 | 54.04 | 56.12 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.2
12 | 1.4 | 12014 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.64 | 30.68 | 31.72 | 32.76 | 33.8 | 35.16 | 36.52 | 37.88 | 39.24 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.48 | 53.56 | 55.64 | 57.72 | 59.8 | 62.08 | 64.36 | 66.64 | 68.92 | 71.2
12 | 1.6 | 12016 | 24.4 | 25.24 | 26.08 | 26.92 | 27.76 | 28.6 | 29.76 | 30.92 | 32.08 | 33.24 | 34.4 | 35.84 | 37.28 | 38.72 | 40.16 | 41.6 | 43.36 | 45.12 | 46.88 | 48.64 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8 | 63.2 | 65.6 | 68 | 70.4 | 72.8
12 | 1.8 | 12018 | 25 | 25.92 | 26.84 | 27.76 | 28.68 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4 | 36.84 | 38.28 | 39.72 | 41.16 | 42.6 | 44.48 | 46.36 | 48.24 | 50.12 | 52 | 54.08 | 56.16 | 58.24 | 60.32 | 62.4 | 64.88 | 67.36 | 69.84 | 72.32 | 74.8
12 | 2 | 12020 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.32 | 32.44 | 33.56 | 34.68 | 35.8 | 37.28 | 38.76 | 40.24 | 41.72 | 43.2 | 45.16 | 47.12 | 49.08 | 51.04 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64 | 66.48 | 68.96 | 71.44 | 73.92 | 76.4
12 | 2.2 | 12022 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.08 | 47.96 | 49.84 | 51.72 | 53.6 | 55.88 | 58.16 | 60.44 | 62.72 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78
12 | 2.4 | 12024 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.08 | 48.96 | 50.84 | 52.72 | 54.6 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 79.6
12 | 2.6 | 12026 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 33.04 | 34.28 | 35.52 | 36.76 | 38 | 39.64 | 41.28 | 42.92 | 44.56 | 46.2 | 48.2 | 50.2 | 52.2 | 54.2 | 56.2 | 58.48 | 60.76 | 63.04 | 65.32 | 67.6 | 70.4 | 73.2 | 76 | 78.8 | 81.6
12 | 2.8 | 12028 | 27 | 28.04 | 29.08 | 30.12 | 31.16 | 32.2 | 33.56 | 34.92 | 36.28 | 37.64 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.88 | 50.96 | 53.04 | 55.12 | 57.2 | 59.6 | 62 | 64.4 | 66.8 | 69.2 | 72 | 74.8 | 77.6 | 80.4 | 83.2
12 | 3 | 12030 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8 | 34.16 | 35.52 | 36.88 | 38.24 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.88 | 51.96 | 54.04 | 56.12 | 58.2 | 60.6 | 63 | 65.4 | 67.8 | 70.2 | 73 | 75.8 | 78.6 | 81.4 | 84.2
13 | 0 | 13000 | 19.2 | 20.08 | 20.96 | 21.84 | 22.72 | 23.6 | 24.44 | 25.28 | 26.12 | 26.96 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.24 | 42.68 | 44.12 | 45.56 | 47 | 48.84 | 50.68 | 52.52 | 54.36 | 56.2
13 | 0.4 | 13004 | 19.2 | 20.08 | 20.96 | 21.84 | 22.72 | 23.6 | 24.44 | 25.28 | 26.12 | 26.96 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.24 | 42.68 | 44.12 | 45.56 | 47 | 48.84 | 50.68 | 52.52 | 54.36 | 56.2
13 | 0.6 | 13006 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6 | 35.84 | 37.08 | 38.32 | 39.56 | 40.8 | 42.44 | 44.08 | 45.72 | 47.36 | 49 | 50.92 | 52.84 | 54.76 | 56.68 | 58.6
13 | 0.8 | 13008 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.36 | 26.32 | 27.28 | 28.24 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.44 | 37.88 | 39.32 | 40.76 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4 | 52.32 | 54.24 | 56.16 | 58.08 | 60
13 | 1 | 13010 | 21.2 | 21.96 | 22.72 | 23.48 | 24.24 | 25 | 25.96 | 26.92 | 27.88 | 28.84 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.92 | 46.64 | 48.36 | 50.08 | 51.8 | 53.92 | 56.04 | 58.16 | 60.28 | 62.4
13 | 1.2 | 13012 | 21.6 | 22.36 | 23.12 | 23.88 | 24.64 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.56 | 32.92 | 34.28 | 35.64 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 46.12 | 48.04 | 49.96 | 51.88 | 53.8 | 55.8 | 57.8 | 59.8 | 61.8 | 63.8
13 | 1.4 | 13014 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.36 | 28.32 | 29.28 | 30.24 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 39.04 | 40.68 | 42.32 | 43.96 | 45.6 | 47.52 | 49.44 | 51.36 | 53.28 | 55.2 | 57.32 | 59.44 | 61.56 | 63.68 | 65.8
13 | 1.6 | 13016 | 22.6 | 23.36 | 24.12 | 24.88 | 25.64 | 26.4 | 27.44 | 28.48 | 29.52 | 30.56 | 31.6 | 32.96 | 34.32 | 35.68 | 37.04 | 38.4 | 40.04 | 41.68 | 43.32 | 44.96 | 46.6 | 48.52 | 50.44 | 52.36 | 54.28 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.2
13 | 1.8 | 13018 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.44 | 29.48 | 30.52 | 31.56 | 32.6 | 33.96 | 35.32 | 36.68 | 38.04 | 39.4 | 41.12 | 42.84 | 44.56 | 46.28 | 48 | 49.92 | 51.84 | 53.76 | 55.68 | 57.6 | 59.92 | 62.24 | 64.56 | 66.88 | 69.2
13 | 2 | 13020 | 23 | 23.96 | 24.92 | 25.88 | 26.84 | 27.8 | 28.88 | 29.96 | 31.04 | 32.12 | 33.2 | 34.52 | 35.84 | 37.16 | 38.48 | 39.8 | 41.64 | 43.48 | 45.32 | 47.16 | 49 | 51 | 53 | 55 | 57 | 59 | 61.32 | 63.64 | 65.96 | 68.28 | 70.6
13 | 2.2 | 13022 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 35.04 | 36.48 | 37.92 | 39.36 | 40.8 | 42.52 | 44.24 | 45.96 | 47.68 | 49.4 | 51.52 | 53.64 | 55.76 | 57.88 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72
13 | 2.4 | 13024 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6 | 36.04 | 37.48 | 38.92 | 40.36 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.6 | 54.8 | 57 | 59.2 | 61.4 | 63.8 | 66.2 | 68.6 | 71 | 73.4
13 | 2.6 | 13026 | 24.4 | 25.36 | 26.32 | 27.28 | 28.24 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.56 | 38.12 | 39.68 | 41.24 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 51.8 | 53.92 | 56.04 | 58.16 | 60.28 | 62.4 | 65 | 67.6 | 70.2 | 72.8 | 75.4
13 | 2.8 | 13028 | 25 | 25.96 | 26.92 | 27.88 | 28.84 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 45.12 | 47.04 | 48.96 | 50.88 | 52.8 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66.4 | 69 | 71.6 | 74.2 | 76.8
13 | 3 | 13030 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.12 | 48.04 | 49.96 | 51.88 | 53.8 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67.4 | 70 | 72.6 | 75.2 | 77.8
14 | 0 | 14000 | 17.6 | 18.44 | 19.28 | 20.12 | 20.96 | 21.8 | 22.52 | 23.24 | 23.96 | 24.68 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.72 | 39.04 | 40.36 | 41.68 | 43 | 44.72 | 46.44 | 48.16 | 49.88 | 51.6
14 | 0.4 | 14004 | 17.6 | 18.44 | 19.28 | 20.12 | 20.96 | 21.8 | 22.52 | 23.24 | 23.96 | 24.68 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.72 | 39.04 | 40.36 | 41.68 | 43 | 44.72 | 46.44 | 48.16 | 49.88 | 51.6
14 | 0.6 | 14006 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4 | 38.92 | 40.44 | 41.96 | 43.48 | 45 | 46.76 | 48.52 | 50.28 | 52.04 | 53.8
14 | 0.8 | 14008 | 18.8 | 19.48 | 20.16 | 20.84 | 21.52 | 22.2 | 23.08 | 23.96 | 24.84 | 25.72 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.32 | 34.64 | 35.96 | 37.28 | 38.6 | 40.12 | 41.64 | 43.16 | 44.68 | 46.2 | 47.96 | 49.72 | 51.48 | 53.24 | 55
14 | 1 | 14010 | 19.6 | 20.28 | 20.96 | 21.64 | 22.32 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.52 | 29.64 | 30.76 | 31.88 | 33 | 34.32 | 35.64 | 36.96 | 38.28 | 39.6 | 41.16 | 42.72 | 44.28 | 45.84 | 47.4 | 49.36 | 51.32 | 53.28 | 55.24 | 57.2
14 | 1.2 | 14012 | 19.8 | 20.48 | 21.16 | 21.84 | 22.52 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6 | 28.88 | 30.16 | 31.44 | 32.72 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.2 | 53 | 54.8 | 56.6 | 58.4
14 | 1.4 | 14014 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.08 | 25.96 | 26.84 | 27.72 | 28.6 | 29.72 | 30.84 | 31.96 | 33.08 | 34.2 | 35.72 | 37.24 | 38.76 | 40.28 | 41.8 | 43.56 | 45.32 | 47.08 | 48.84 | 50.6 | 52.56 | 54.52 | 56.48 | 58.44 | 60.4
14 | 1.6 | 14016 | 20.8 | 21.48 | 22.16 | 22.84 | 23.52 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 30.08 | 31.36 | 32.64 | 33.92 | 35.2 | 36.72 | 38.24 | 39.76 | 41.28 | 42.8 | 44.56 | 46.32 | 48.08 | 49.84 | 51.6 | 53.6 | 55.6 | 57.6 | 59.6 | 61.6
14 | 1.8 | 14018 | 21 | 21.84 | 22.68 | 23.52 | 24.36 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 31.08 | 32.36 | 33.64 | 34.92 | 36.2 | 37.76 | 39.32 | 40.88 | 42.44 | 44 | 45.76 | 47.52 | 49.28 | 51.04 | 52.8 | 54.96 | 57.12 | 59.28 | 61.44 | 63.6
14 | 2 | 14020 | 21 | 21.88 | 22.76 | 23.64 | 24.52 | 25.4 | 26.44 | 27.48 | 28.52 | 29.56 | 30.6 | 31.76 | 32.92 | 34.08 | 35.24 | 36.4 | 38.12 | 39.84 | 41.56 | 43.28 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.16 | 58.32 | 60.48 | 62.64 | 64.8
14 | 2.2 | 14022 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.16 | 49.12 | 51.08 | 53.04 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66
14 | 2.4 | 14024 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8 | 33.12 | 34.44 | 35.76 | 37.08 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.2 | 50.2 | 52.2 | 54.2 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.2
14 | 2.6 | 14026 | 22.2 | 23.08 | 23.96 | 24.84 | 25.72 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.48 | 34.96 | 36.44 | 37.92 | 39.4 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49.36 | 51.32 | 53.28 | 55.24 | 57.2 | 59.6 | 62 | 64.4 | 66.8 | 69.2
14 | 2.8 | 14028 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.52 | 29.64 | 30.76 | 31.88 | 33 | 34.32 | 35.64 | 36.96 | 38.28 | 39.6 | 41.36 | 43.12 | 44.88 | 46.64 | 48.4 | 50.4 | 52.4 | 54.4 | 56.4 | 58.4 | 60.8 | 63.2 | 65.6 | 68 | 70.4
14 | 3 | 14030 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.68 | 36.16 | 37.64 | 39.12 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.4 | 53.4 | 55.4 | 57.4 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.4
15 | 0 | 15000 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
15 | 0.4 | 15004 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
15 | 0.6 | 15006 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49
15 | 0.8 | 15008 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50
15 | 1 | 15010 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52
15 | 1.2 | 15012 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26.2 | 27.4 | 28.6 | 29.8 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.6 | 48.2 | 49.8 | 51.4 | 53
15 | 1.4 | 15014 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27 | 28 | 29 | 30 | 31 | 32.4 | 33.8 | 35.2 | 36.6 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55
15 | 1.6 | 15016 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56
15 | 1.8 | 15018 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 23.8 | 24.6 | 25.4 | 26.2 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 50 | 52 | 54 | 56 | 58
15 | 2 | 15020 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.6 | 36.2 | 37.8 | 39.4 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51 | 53 | 55 | 57 | 59
15 | 2.2 | 15022 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 52 | 54 | 56 | 58 | 60
15 | 2.4 | 15024 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53 | 55 | 57 | 59 | 61
15 | 2.6 | 15026 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.4 | 31.8 | 33.2 | 34.6 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63
15 | 2.8 | 15028 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.6 | 39.2 | 40.8 | 42.4 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64
15 | 3 | 15030 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.4 | 32.8 | 34.2 | 35.6 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65
16 | 0 | 16000 | 15.2 | 15.96 | 16.72 | 17.48 | 18.24 | 19 | 19.56 | 20.12 | 20.68 | 21.24 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.56 | 33.72 | 34.88 | 36.04 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6
16 | 0.4 | 16004 | 15.2 | 15.96 | 16.72 | 17.48 | 18.24 | 19 | 19.56 | 20.12 | 20.68 | 21.24 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.56 | 33.72 | 34.88 | 36.04 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6
16 | 0.6 | 16006 | 16.2 | 16.76 | 17.32 | 17.88 | 18.44 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.72 | 24.64 | 25.56 | 26.48 | 27.4 | 28.4 | 29.4 | 30.4 | 31.4 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.48 | 41.96 | 43.44 | 44.92 | 46.4
16 | 0.8 | 16008 | 16.2 | 16.76 | 17.32 | 17.88 | 18.44 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40 | 41.52 | 43.04 | 44.56 | 46.08 | 47.6
16 | 1 | 16010 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.72 | 25.64 | 26.56 | 27.48 | 28.4 | 29.56 | 30.72 | 31.88 | 33.04 | 34.2 | 35.56 | 36.92 | 38.28 | 39.64 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4
16 | 1.2 | 16012 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.92 | 26.04 | 27.16 | 28.28 | 29.4 | 30.56 | 31.72 | 32.88 | 34.04 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.16 | 45.72 | 47.28 | 48.84 | 50.4
16 | 1.4 | 16014 | 17.2 | 17.92 | 18.64 | 19.36 | 20.08 | 20.8 | 21.56 | 22.32 | 23.08 | 23.84 | 24.6 | 25.56 | 26.52 | 27.48 | 28.44 | 29.4 | 30.72 | 32.04 | 33.36 | 34.68 | 36 | 37.52 | 39.04 | 40.56 | 42.08 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2
16 | 1.6 | 16016 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.76 | 22.52 | 23.28 | 24.04 | 24.8 | 25.92 | 27.04 | 28.16 | 29.28 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.52 | 40.04 | 41.56 | 43.08 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2
16 | 1.8 | 16018 | 18 | 18.76 | 19.52 | 20.28 | 21.04 | 21.8 | 22.56 | 23.32 | 24.08 | 24.84 | 25.6 | 26.76 | 27.92 | 29.08 | 30.24 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.48 | 49.36 | 51.24 | 53.12 | 55
16 | 2 | 16020 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.88 | 34.36 | 35.84 | 37.32 | 38.8 | 40.36 | 41.92 | 43.48 | 45.04 | 46.6 | 48.48 | 50.36 | 52.24 | 54.12 | 56
16 | 2.2 | 16022 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 22.92 | 23.84 | 24.76 | 25.68 | 26.6 | 27.76 | 28.92 | 30.08 | 31.24 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.72 | 42.44 | 44.16 | 45.88 | 47.6 | 49.48 | 51.36 | 53.24 | 55.12 | 57
16 | 2.4 | 16024 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40 | 41.68 | 43.36 | 45.04 | 46.72 | 48.4 | 50.32 | 52.24 | 54.16 | 56.08 | 58
16 | 2.6 | 16026 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.92 | 30.24 | 31.56 | 32.88 | 34.2 | 35.52 | 36.84 | 38.16 | 39.48 | 40.8 | 42.52 | 44.24 | 45.96 | 47.68 | 49.4 | 51.48 | 53.56 | 55.64 | 57.72 | 59.8
16 | 2.8 | 16028 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.72 | 25.64 | 26.56 | 27.48 | 28.4 | 29.56 | 30.72 | 31.88 | 33.04 | 34.2 | 35.72 | 37.24 | 38.76 | 40.28 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8
16 | 3 | 16030 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.76 | 25.72 | 26.68 | 27.64 | 28.6 | 29.92 | 31.24 | 32.56 | 33.88 | 35.2 | 36.72 | 38.24 | 39.76 | 41.28 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.48 | 55.56 | 57.64 | 59.72 | 61.8
17 | 0 | 17000 | 14.4 | 15.12 | 15.84 | 16.56 | 17.28 | 18 | 18.52 | 19.04 | 19.56 | 20.08 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
17 | 0.4 | 17004 | 14.4 | 15.12 | 15.84 | 16.56 | 17.28 | 18 | 18.52 | 19.04 | 19.56 | 20.08 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
17 | 0.6 | 17006 | 15.4 | 15.92 | 16.44 | 16.96 | 17.48 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.44 | 23.28 | 24.12 | 24.96 | 25.8 | 26.8 | 27.8 | 28.8 | 29.8 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8
17 | 0.8 | 17008 | 15.4 | 15.92 | 16.44 | 16.96 | 17.48 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.24 | 28.28 | 29.32 | 30.36 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.44 | 40.88 | 42.32 | 43.76 | 45.2
17 | 1 | 17010 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.44 | 24.28 | 25.12 | 25.96 | 26.8 | 27.92 | 29.04 | 30.16 | 31.28 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8
17 | 1.2 | 17012 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.64 | 24.68 | 25.72 | 26.76 | 27.8 | 28.92 | 30.04 | 31.16 | 32.28 | 33.4 | 34.76 | 36.12 | 37.48 | 38.84 | 40.2 | 41.72 | 43.24 | 44.76 | 46.28 | 47.8
17 | 1.4 | 17014 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.32 | 21.04 | 21.76 | 22.48 | 23.2 | 24.12 | 25.04 | 25.96 | 26.88 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.44 | 36.88 | 38.32 | 39.76 | 41.2 | 42.84 | 44.48 | 46.12 | 47.76 | 49.4
17 | 1.6 | 17016 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.72 | 21.44 | 22.16 | 22.88 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.44 | 37.88 | 39.32 | 40.76 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4
17 | 1.8 | 17018 | 17 | 17.72 | 18.44 | 19.16 | 19.88 | 20.6 | 21.32 | 22.04 | 22.76 | 23.48 | 24.2 | 25.32 | 26.44 | 27.56 | 28.68 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52
17 | 2 | 17020 | 17.4 | 18.04 | 18.68 | 19.32 | 19.96 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 31.16 | 32.52 | 33.88 | 35.24 | 36.6 | 38.12 | 39.64 | 41.16 | 42.68 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53
17 | 2.2 | 17022 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.84 | 22.68 | 23.52 | 24.36 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.64 | 40.28 | 41.92 | 43.56 | 45.2 | 46.96 | 48.72 | 50.48 | 52.24 | 54
17 | 2.4 | 17024 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.24 | 28.28 | 29.32 | 30.36 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.64 | 49.48 | 51.32 | 53.16 | 55
17 | 2.6 | 17026 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.44 | 28.68 | 29.92 | 31.16 | 32.4 | 33.64 | 34.88 | 36.12 | 37.36 | 38.6 | 40.24 | 41.88 | 43.52 | 45.16 | 46.8 | 48.76 | 50.72 | 52.68 | 54.64 | 56.6
17 | 2.8 | 17028 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.44 | 24.28 | 25.12 | 25.96 | 26.8 | 27.92 | 29.04 | 30.16 | 31.28 | 32.4 | 33.84 | 35.28 | 36.72 | 38.16 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6
17 | 3 | 17030 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.52 | 24.44 | 25.36 | 26.28 | 27.2 | 28.44 | 29.68 | 30.92 | 32.16 | 33.4 | 34.84 | 36.28 | 37.72 | 39.16 | 40.6 | 42.24 | 43.88 | 45.52 | 47.16 | 48.8 | 50.76 | 52.72 | 54.68 | 56.64 | 58.6
18 | 0 | 18000 | 13.6 | 14.28 | 14.96 | 15.64 | 16.32 | 17 | 17.48 | 17.96 | 18.44 | 18.92 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.28 | 30.36 | 31.44 | 32.52 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8
18 | 0.4 | 18004 | 13.6 | 14.28 | 14.96 | 15.64 | 16.32 | 17 | 17.48 | 17.96 | 18.44 | 18.92 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.28 | 30.36 | 31.44 | 32.52 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8
18 | 0.6 | 18006 | 14.6 | 15.08 | 15.56 | 16.04 | 16.52 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.16 | 21.92 | 22.68 | 23.44 | 24.2 | 25.2 | 26.2 | 27.2 | 28.2 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.24 | 37.48 | 38.72 | 39.96 | 41.2
18 | 0.8 | 18008 | 14.6 | 15.08 | 15.56 | 16.04 | 16.52 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.76 | 26.72 | 27.68 | 28.64 | 29.6 | 30.88 | 32.16 | 33.44 | 34.72 | 36 | 37.36 | 38.72 | 40.08 | 41.44 | 42.8
18 | 1 | 18010 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.16 | 22.92 | 23.68 | 24.44 | 25.2 | 26.28 | 27.36 | 28.44 | 29.52 | 30.6 | 31.88 | 33.16 | 34.44 | 35.72 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2
18 | 1.2 | 18012 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.36 | 23.32 | 24.28 | 25.24 | 26.2 | 27.28 | 28.36 | 29.44 | 30.52 | 31.6 | 32.84 | 34.08 | 35.32 | 36.56 | 37.8 | 39.28 | 40.76 | 42.24 | 43.72 | 45.2
18 | 1.4 | 18014 | 15.6 | 16.16 | 16.72 | 17.28 | 17.84 | 18.4 | 19.08 | 19.76 | 20.44 | 21.12 | 21.8 | 22.68 | 23.56 | 24.44 | 25.32 | 26.2 | 27.36 | 28.52 | 29.68 | 30.84 | 32 | 33.36 | 34.72 | 36.08 | 37.44 | 38.8 | 40.36 | 41.92 | 43.48 | 45.04 | 46.6
18 | 1.6 | 18016 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.68 | 20.36 | 21.04 | 21.72 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.36 | 35.72 | 37.08 | 38.44 | 39.8 | 41.36 | 42.92 | 44.48 | 46.04 | 47.6
18 | 1.8 | 18018 | 16 | 16.68 | 17.36 | 18.04 | 18.72 | 19.4 | 20.08 | 20.76 | 21.44 | 22.12 | 22.8 | 23.88 | 24.96 | 26.04 | 27.12 | 28.2 | 29.36 | 30.52 | 31.68 | 32.84 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.44 | 44.08 | 45.72 | 47.36 | 49
18 | 2 | 18020 | 16.6 | 17.16 | 17.72 | 18.28 | 18.84 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.44 | 30.68 | 31.92 | 33.16 | 34.4 | 35.88 | 37.36 | 38.84 | 40.32 | 41.8 | 43.44 | 45.08 | 46.72 | 48.36 | 50
18 | 2.2 | 18022 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.88 | 25.96 | 27.04 | 28.12 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.56 | 38.12 | 39.68 | 41.24 | 42.8 | 44.44 | 46.08 | 47.72 | 49.36 | 51
18 | 2.4 | 18024 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.76 | 26.72 | 27.68 | 28.64 | 29.6 | 30.88 | 32.16 | 33.44 | 34.72 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52
18 | 2.6 | 18026 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.96 | 27.12 | 28.28 | 29.44 | 30.6 | 31.76 | 32.92 | 34.08 | 35.24 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.04 | 47.88 | 49.72 | 51.56 | 53.4
18 | 2.8 | 18028 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.16 | 22.92 | 23.68 | 24.44 | 25.2 | 26.28 | 27.36 | 28.44 | 29.52 | 30.6 | 31.96 | 33.32 | 34.68 | 36.04 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.04 | 48.88 | 50.72 | 52.56 | 54.4
18 | 3 | 18030 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.28 | 23.16 | 24.04 | 24.92 | 25.8 | 26.96 | 28.12 | 29.28 | 30.44 | 31.6 | 32.96 | 34.32 | 35.68 | 37.04 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.04 | 49.88 | 51.72 | 53.56 | 55.4
19 | 0 | 19000 | 12.8 | 13.44 | 14.08 | 14.72 | 15.36 | 16 | 16.44 | 16.88 | 17.32 | 17.76 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4
19 | 0.4 | 19004 | 12.8 | 13.44 | 14.08 | 14.72 | 15.36 | 16 | 16.44 | 16.88 | 17.32 | 17.76 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4
19 | 0.6 | 19006 | 13.8 | 14.24 | 14.68 | 15.12 | 15.56 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 19.88 | 20.56 | 21.24 | 21.92 | 22.6 | 23.6 | 24.6 | 25.6 | 26.6 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.12 | 35.24 | 36.36 | 37.48 | 38.6
19 | 0.8 | 19008 | 13.8 | 14.24 | 14.68 | 15.12 | 15.56 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.28 | 25.16 | 26.04 | 26.92 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.28 | 36.56 | 37.84 | 39.12 | 40.4
19 | 1 | 19010 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 20.88 | 21.56 | 22.24 | 22.92 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6
19 | 1.2 | 19012 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 21.08 | 21.96 | 22.84 | 23.72 | 24.6 | 25.64 | 26.68 | 27.72 | 28.76 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.84 | 38.28 | 39.72 | 41.16 | 42.6
19 | 1.4 | 19014 | 14.8 | 15.28 | 15.76 | 16.24 | 16.72 | 17.2 | 17.84 | 18.48 | 19.12 | 19.76 | 20.4 | 21.24 | 22.08 | 22.92 | 23.76 | 24.6 | 25.68 | 26.76 | 27.84 | 28.92 | 30 | 31.28 | 32.56 | 33.84 | 35.12 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8
19 | 1.6 | 19016 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.64 | 19.28 | 19.92 | 20.56 | 21.2 | 22.08 | 22.96 | 23.84 | 24.72 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.28 | 33.56 | 34.84 | 36.12 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8
19 | 1.8 | 19018 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.84 | 19.48 | 20.12 | 20.76 | 21.4 | 22.44 | 23.48 | 24.52 | 25.56 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.92 | 41.44 | 42.96 | 44.48 | 46
19 | 2 | 19020 | 15.8 | 16.28 | 16.76 | 17.24 | 17.72 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.72 | 28.84 | 29.96 | 31.08 | 32.2 | 33.64 | 35.08 | 36.52 | 37.96 | 39.4 | 40.92 | 42.44 | 43.96 | 45.48 | 47
19 | 2.2 | 19022 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.68 | 20.36 | 21.04 | 21.72 | 22.4 | 23.44 | 24.48 | 25.52 | 26.56 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.48 | 35.96 | 37.44 | 38.92 | 40.4 | 41.92 | 43.44 | 44.96 | 46.48 | 48
19 | 2.4 | 19024 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.28 | 25.16 | 26.04 | 26.92 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.28 | 43.96 | 45.64 | 47.32 | 49
19 | 2.6 | 19026 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.48 | 25.56 | 26.64 | 27.72 | 28.8 | 29.88 | 30.96 | 32.04 | 33.12 | 34.2 | 35.68 | 37.16 | 38.64 | 40.12 | 41.6 | 43.32 | 45.04 | 46.76 | 48.48 | 50.2
19 | 2.8 | 19028 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 20.88 | 21.56 | 22.24 | 22.92 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.08 | 31.36 | 32.64 | 33.92 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.32 | 46.04 | 47.76 | 49.48 | 51.2
19 | 3 | 19030 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 21.04 | 21.88 | 22.72 | 23.56 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 31.08 | 32.36 | 33.64 | 34.92 | 36.2 | 37.68 | 39.16 | 40.64 | 42.12 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2
20 | 0 | 20000 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
20 | 0.4 | 20004 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
20 | 0.6 | 20006 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36
20 | 0.8 | 20008 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38
20 | 1 | 20010 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 23 | 24 | 25 | 26 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39
20 | 1.2 | 20012 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40
20 | 1.4 | 20014 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41
20 | 1.6 | 20016 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42
20 | 1.8 | 20018 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43
20 | 2 | 20020 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.4 | 32.8 | 34.2 | 35.6 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44
20 | 2.2 | 20022 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32.4 | 33.8 | 35.2 | 36.6 | 38 | 39.4 | 40.8 | 42.2 | 43.6 | 45
20 | 2.4 | 20024 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46
20 | 2.6 | 20026 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
20 | 2.8 | 20028 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 23 | 24 | 25 | 26 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48
20 | 3 | 20030 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49
21 | 0 | 21000 | 11.2 | 11.76 | 12.32 | 12.88 | 13.44 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6
21 | 0.4 | 21004 | 11.2 | 11.76 | 12.32 | 12.88 | 13.44 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6
21 | 0.6 | 21006 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.36 | 17.92 | 18.48 | 19.04 | 19.6 | 20.52 | 21.44 | 22.36 | 23.28 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 29.76 | 30.72 | 31.68 | 32.64 | 33.6
21 | 0.8 | 21008 | 12.2 | 12.56 | 12.92 | 13.28 | 13.64 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4
21 | 1 | 21010 | 12.2 | 12.72 | 13.24 | 13.76 | 14.28 | 14.8 | 15.36 | 15.92 | 16.48 | 17.04 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4
21 | 1.2 | 21012 | 12.2 | 12.76 | 13.32 | 13.88 | 14.44 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.52 | 19.24 | 19.96 | 20.68 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 26.96 | 27.92 | 28.88 | 29.84 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4
21 | 1.4 | 21014 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.32 | 28.44 | 29.56 | 30.68 | 31.8 | 33.08 | 34.36 | 35.64 | 36.92 | 38.2
21 | 1.6 | 21016 | 13 | 13.56 | 14.12 | 14.68 | 15.24 | 15.8 | 16.36 | 16.92 | 17.48 | 18.04 | 18.6 | 19.36 | 20.12 | 20.88 | 21.64 | 22.4 | 23.32 | 24.24 | 25.16 | 26.08 | 27 | 28.12 | 29.24 | 30.36 | 31.48 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2
21 | 1.8 | 21018 | 13.2 | 13.72 | 14.24 | 14.76 | 15.28 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.68 | 20.56 | 21.44 | 22.32 | 23.2 | 24.16 | 25.12 | 26.08 | 27.04 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2
21 | 2 | 21020 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.32 | 30.64 | 31.96 | 33.28 | 34.6 | 35.88 | 37.16 | 38.44 | 39.72 | 41
21 | 2.2 | 21022 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.36 | 17.92 | 18.48 | 19.04 | 19.6 | 20.52 | 21.44 | 22.36 | 23.28 | 24.2 | 25.16 | 26.12 | 27.08 | 28.04 | 29 | 30.28 | 31.56 | 32.84 | 34.12 | 35.4 | 36.72 | 38.04 | 39.36 | 40.68 | 42
21 | 2.4 | 21024 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.52 | 18.24 | 18.96 | 19.68 | 20.4 | 21.16 | 21.92 | 22.68 | 23.44 | 24.2 | 25.32 | 26.44 | 27.56 | 28.68 | 29.8 | 30.96 | 32.12 | 33.28 | 34.44 | 35.6 | 37.08 | 38.56 | 40.04 | 41.52 | 43
21 | 2.6 | 21026 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.16 | 27.12 | 28.08 | 29.04 | 30 | 31.28 | 32.56 | 33.84 | 35.12 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8
21 | 2.8 | 21028 | 14.8 | 15.36 | 15.92 | 16.48 | 17.04 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8
21 | 3 | 21030 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.52 | 19.24 | 19.96 | 20.68 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 27.12 | 28.24 | 29.36 | 30.48 | 31.6 | 32.92 | 34.24 | 35.56 | 36.88 | 38.2 | 39.68 | 41.16 | 42.64 | 44.12 | 45.6
22 | 0 | 22000 | 10.4 | 10.92 | 11.44 | 11.96 | 12.48 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2
22 | 0.4 | 22004 | 10.4 | 10.92 | 11.44 | 11.96 | 12.48 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2
22 | 0.6 | 22006 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.12 | 16.64 | 17.16 | 17.68 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.52 | 28.44 | 29.36 | 30.28 | 31.2
22 | 0.8 | 22008 | 11.4 | 11.72 | 12.04 | 12.36 | 12.68 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.32 | 17.04 | 17.76 | 18.48 | 19.2 | 19.92 | 20.64 | 21.36 | 22.08 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8
22 | 1 | 22010 | 11.4 | 11.84 | 12.28 | 12.72 | 13.16 | 13.6 | 14.12 | 14.64 | 15.16 | 15.68 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.64 | 30.68 | 31.72 | 32.76 | 33.8
22 | 1.2 | 22012 | 11.4 | 11.92 | 12.44 | 12.96 | 13.48 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.24 | 17.88 | 18.52 | 19.16 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 24.92 | 25.84 | 26.76 | 27.68 | 28.6 | 29.84 | 31.08 | 32.32 | 33.56 | 34.8
22 | 1.4 | 22014 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.32 | 18.04 | 18.76 | 19.48 | 20.2 | 21.04 | 21.88 | 22.72 | 23.56 | 24.4 | 25.44 | 26.48 | 27.52 | 28.56 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4
22 | 1.6 | 22016 | 12 | 12.52 | 13.04 | 13.56 | 14.08 | 14.6 | 15.12 | 15.64 | 16.16 | 16.68 | 17.2 | 17.92 | 18.64 | 19.36 | 20.08 | 20.8 | 21.64 | 22.48 | 23.32 | 24.16 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4
22 | 1.8 | 22018 | 12.4 | 12.84 | 13.28 | 13.72 | 14.16 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.36 | 19.12 | 19.88 | 20.64 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4
22 | 2 | 22020 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 27.24 | 28.48 | 29.72 | 30.96 | 32.2 | 33.36 | 34.52 | 35.68 | 36.84 | 38
22 | 2.2 | 22022 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.12 | 16.64 | 17.16 | 17.68 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.32 | 24.24 | 25.16 | 26.08 | 27 | 28.16 | 29.32 | 30.48 | 31.64 | 32.8 | 34.04 | 35.28 | 36.52 | 37.76 | 39
22 | 2.4 | 22024 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.24 | 16.88 | 17.52 | 18.16 | 18.8 | 19.52 | 20.24 | 20.96 | 21.68 | 22.4 | 23.44 | 24.48 | 25.52 | 26.56 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40
22 | 2.6 | 22026 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.32 | 17.04 | 17.76 | 18.48 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.16 | 30.32 | 31.48 | 32.64 | 33.8 | 35.16 | 36.52 | 37.88 | 39.24 | 40.6
22 | 2.8 | 22028 | 13.6 | 14.12 | 14.64 | 15.16 | 15.68 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.84 | 31.08 | 32.32 | 33.56 | 34.8 | 36.16 | 37.52 | 38.88 | 40.24 | 41.6
22 | 3 | 22030 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.24 | 17.88 | 18.52 | 19.16 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 25.04 | 26.08 | 27.12 | 28.16 | 29.2 | 30.44 | 31.68 | 32.92 | 34.16 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
23 | 0 | 23000 | 9.6 | 10.08 | 10.56 | 11.04 | 11.52 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8
23 | 0.4 | 23004 | 9.6 | 10.08 | 10.56 | 11.04 | 11.52 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8
23 | 0.6 | 23006 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.88 | 15.36 | 15.84 | 16.32 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.28 | 26.16 | 27.04 | 27.92 | 28.8
23 | 0.8 | 23008 | 10.6 | 10.88 | 11.16 | 11.44 | 11.72 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 15.08 | 15.76 | 16.44 | 17.12 | 17.8 | 18.48 | 19.16 | 19.84 | 20.52 | 21.2 | 22.04 | 22.88 | 23.72 | 24.56 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2
23 | 1 | 23010 | 10.6 | 10.96 | 11.32 | 11.68 | 12.04 | 12.4 | 12.88 | 13.36 | 13.84 | 14.32 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.36 | 28.32 | 29.28 | 30.24 | 31.2
23 | 1.2 | 23012 | 10.6 | 11.08 | 11.56 | 12.04 | 12.52 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 15.96 | 16.52 | 17.08 | 17.64 | 18.2 | 18.96 | 19.72 | 20.48 | 21.24 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.56 | 28.72 | 29.88 | 31.04 | 32.2
23 | 1.4 | 23014 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.56 | 20.32 | 21.08 | 21.84 | 22.6 | 23.56 | 24.52 | 25.48 | 26.44 | 27.4 | 28.44 | 29.48 | 30.52 | 31.56 | 32.6
23 | 1.6 | 23016 | 11 | 11.48 | 11.96 | 12.44 | 12.92 | 13.4 | 13.88 | 14.36 | 14.84 | 15.32 | 15.8 | 16.48 | 17.16 | 17.84 | 18.52 | 19.2 | 19.96 | 20.72 | 21.48 | 22.24 | 23 | 23.96 | 24.92 | 25.88 | 26.84 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6
23 | 1.8 | 23018 | 11.6 | 11.96 | 12.32 | 12.68 | 13.04 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.48 | 21.36 | 22.24 | 23.12 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6
23 | 2 | 23020 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 25.16 | 26.32 | 27.48 | 28.64 | 29.8 | 30.84 | 31.88 | 32.92 | 33.96 | 35
23 | 2.2 | 23022 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.88 | 15.36 | 15.84 | 16.32 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.48 | 22.36 | 23.24 | 24.12 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.36 | 32.52 | 33.68 | 34.84 | 36
23 | 2.4 | 23024 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.96 | 15.52 | 16.08 | 16.64 | 17.2 | 17.88 | 18.56 | 19.24 | 19.92 | 20.6 | 21.56 | 22.52 | 23.48 | 24.44 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37
23 | 2.6 | 23026 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 15.08 | 15.76 | 16.44 | 17.12 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.48 | 23.36 | 24.24 | 25.12 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4
23 | 2.8 | 23028 | 12.4 | 12.88 | 13.36 | 13.84 | 14.32 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.56 | 28.72 | 29.88 | 31.04 | 32.2 | 33.44 | 34.68 | 35.92 | 37.16 | 38.4
23 | 3 | 23030 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 15.96 | 16.52 | 17.08 | 17.64 | 18.2 | 18.96 | 19.72 | 20.48 | 21.24 | 22 | 22.96 | 23.92 | 24.88 | 25.84 | 26.8 | 27.96 | 29.12 | 30.28 | 31.44 | 32.6 | 33.84 | 35.08 | 36.32 | 37.56 | 38.8
24 | 0 | 24000 | 8.8 | 9.24 | 9.68 | 10.12 | 10.56 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4
24 | 0.4 | 24004 | 8.8 | 9.24 | 9.68 | 10.12 | 10.56 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4
24 | 0.6 | 24006 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.64 | 14.08 | 14.52 | 14.96 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.48 | 20.16 | 20.84 | 21.52 | 22.2 | 23.04 | 23.88 | 24.72 | 25.56 | 26.4
24 | 0.8 | 24008 | 9.8 | 10.04 | 10.28 | 10.52 | 10.76 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.84 | 14.48 | 15.12 | 15.76 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.32 | 21.04 | 21.76 | 22.48 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6
24 | 1 | 24010 | 9.8 | 10.08 | 10.36 | 10.64 | 10.92 | 11.2 | 11.64 | 12.08 | 12.52 | 12.96 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.08 | 25.96 | 26.84 | 27.72 | 28.6
24 | 1.2 | 24012 | 9.8 | 10.24 | 10.68 | 11.12 | 11.56 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.68 | 15.16 | 15.64 | 16.12 | 16.6 | 17.28 | 17.96 | 18.64 | 19.32 | 20 | 20.84 | 21.68 | 22.52 | 23.36 | 24.2 | 25.28 | 26.36 | 27.44 | 28.52 | 29.6
24 | 1.4 | 24014 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.84 | 15.48 | 16.12 | 16.76 | 17.4 | 18.08 | 18.76 | 19.44 | 20.12 | 20.8 | 21.68 | 22.56 | 23.44 | 24.32 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8
24 | 1.6 | 24016 | 10 | 10.44 | 10.88 | 11.32 | 11.76 | 12.2 | 12.64 | 13.08 | 13.52 | 13.96 | 14.4 | 15.04 | 15.68 | 16.32 | 16.96 | 17.6 | 18.28 | 18.96 | 19.64 | 20.32 | 21 | 21.88 | 22.76 | 23.64 | 24.52 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8
24 | 1.8 | 24018 | 10.8 | 11.08 | 11.36 | 11.64 | 11.92 | 12.2 | 12.8 | 13.4 | 14 | 14.6 | 15.2 | 15.72 | 16.24 | 16.76 | 17.28 | 17.8 | 18.64 | 19.48 | 20.32 | 21.16 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8
24 | 2 | 24020 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 23.08 | 24.16 | 25.24 | 26.32 | 27.4 | 28.32 | 29.24 | 30.16 | 31.08 | 32
24 | 2.2 | 24022 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.64 | 14.08 | 14.52 | 14.96 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.64 | 20.48 | 21.32 | 22.16 | 23 | 23.92 | 24.84 | 25.76 | 26.68 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33
24 | 2.4 | 24024 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.68 | 14.16 | 14.64 | 15.12 | 15.6 | 16.24 | 16.88 | 17.52 | 18.16 | 18.8 | 19.68 | 20.56 | 21.44 | 22.32 | 23.2 | 24.24 | 25.28 | 26.32 | 27.36 | 28.4 | 29.52 | 30.64 | 31.76 | 32.88 | 34
24 | 2.6 | 24026 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.84 | 14.48 | 15.12 | 15.76 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 24.92 | 25.84 | 26.76 | 27.68 | 28.6 | 29.72 | 30.84 | 31.96 | 33.08 | 34.2
24 | 2.8 | 24028 | 11.2 | 11.64 | 12.08 | 12.52 | 12.96 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.28 | 26.36 | 27.44 | 28.52 | 29.6 | 30.72 | 31.84 | 32.96 | 34.08 | 35.2
24 | 3 | 24030 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.68 | 15.16 | 15.64 | 16.12 | 16.6 | 17.28 | 17.96 | 18.64 | 19.32 | 20 | 20.88 | 21.76 | 22.64 | 23.52 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4
25 | 0 | 25000 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23
25 | 0.4 | 25004 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23
25 | 0.6 | 25006 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24
25 | 0.8 | 25008 | 9 | 9.2 | 9.4 | 9.6 | 9.8 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25
25 | 1 | 25010 | 9 | 9.2 | 9.4 | 9.6 | 9.8 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26
25 | 1.2 | 25012 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27
25 | 1.4 | 25014 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 23.8 | 24.6 | 25.4 | 26.2 | 27
25 | 1.6 | 25016 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28
25 | 1.8 | 25018 | 10 | 10.2 | 10.4 | 10.6 | 10.8 | 11 | 11.6 | 12.2 | 12.8 | 13.4 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29
25 | 2 | 25020 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 21 | 22 | 23 | 24 | 25 | 25.8 | 26.6 | 27.4 | 28.2 | 29
25 | 2.2 | 25022 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30
25 | 2.4 | 25024 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
25 | 2.6 | 25026 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27 | 28 | 29 | 30 | 31
25 | 2.8 | 25028 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
25 | 3 | 25030 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Notes:
| 1. |  | 6: Table values were obtained by linear interpolation using CT values published in USEPA's Guidance Manual for Compliance with the Filtration and Disinfection
Requirements for Public Water Systems Using Surface Water Sources, March 1991 edition. This table was developed by Nancy Feagin, P.E. of the
Drinking Water Northwest Regional Office
| 2. |  | 6: For other levels of log inactivation, multiply the table values by the log inactivation required. For example, for 0.5 log inactivation multiply the table values by 0.5.
| 3. |  | 6: For systems with pH values exceeding 9.0 see the Interim Enhanced Surface Water Treatment Rule Notice of Data Availability, Federal Register, November 3, 1997.