## Cover Page & Notes
Washington State Department of Health
Rapid Rate Filtration Monthly Report Forms
Notes and Instructions
Version 2.3.2
Report Designed for All Rapid Rate Filtration Plants
[5 empty] | DOH Form |  | 331-527-F
[5 empty] | Revised |  | 2019-04-04
Notes:
This workbook was developed using Microsoft Excel 2000. However, it can be used in Excel 97 as well as later versions with no problems.
The workbook is intended for use by water treatment plant operators to enhance recordkeeping, reporting and legibility.
It is designed to minimize the work necessary to calculate totals, averages, count events, etc.
The SWTR Disinfection Monthly Reports will also look up and calculate required CT values for Giardia inactivation.
Data or calculations that do not comply with standards or requirements will show up in bold, italic text with pink highlighting.
Saving and Using this Workbook as a Template (Optional)
To save this workbook as a template:
Clear out any data input by the user.
Click on File, Save As. When prompted, give it a new file name, and specify the "Save as type" as Template.
Click on Save in the dialog box.
To use as template when starting a new month:
With Microsoft Excel running, click on File, New. The WTP template should show in the "New" dialog box.
Click on the template; it will come up as a regular Excel spreadsheet.
When the spreadsheet is saved for the first time, you will be required to supply a name for the file.
Recommended file name: "WTP_<PWSID>_<Plant ID>_YYMM.xls", where YYMM is the reporting year and month; e.g.: WTP_00050_001_0308.xls.
The advantage of starting a workbook using a template is that you'll always have a blank workbook (without having to clear out an old one)
and minimize the chance of overwriting a previous month's workbook.
The Forms
The workbook consists of three forms:
The Rapid Rate WTP Monthly Rept is for recording information on the operation of a conventional water treatment plant.
The SWTR Monthly Disinfection Rept (DOH Form 331-440-F) is for recording disinfection process information for a plant using Chlorine disinfection.
The Monthly Summary gathers data from the other two forms, plus other provided information and reports
the SWTR compliance status for the month.
Entering Data:
All cells in the workbook are protected, except for those intended for data input by the user.
Cells and columns intended for user input have titles or headings colored blue.
Printing
Because of the size of the Rapid Rate WTP Monthly Rept, it should be printed on legal size paper, in landscape mode, if it is desired to fit on one page.
Use the "Page Setup" menu to choose the paper size and orientation. Change left and right margins to 0.5" and check "Fit to" 1 pg wide by 1 pg tall.
The SWTR Monthly Disinfection Rept and the Monthly Summary each fit on letter size paper in landscape mode.
Where to Send these Report Forms
Send your report forms to the appropriate Office of Drinking Water regional office:
Northwest Drinking Water |  |  |  |  | Southwest Drinking Water |  |  |  | Eastern Drinking Water
Operations |  |  |  |  | Operations |  |  |  | Operations
Department of Health |  |  |  |  | Department of Health |  |  |  | Department of Health
20425 72nd Ave S., Ste 310 |  |  |  |  | P O Box 47823 |  |  |  | 16201 E. Indiana Ave, Suite 1500
Kent, WA 98032-2388 |  |  |  |  | Olympia, WA 98504-7823 |  |  |  | Spokane Valley, WA 99216
253-395-6750 |  |  |  |  | 360-236-3030 |  |  |  | 509-329-2100
| Fax: 253-395-6760 |  |  |  | Fax: 360-664-8058 |  |  |  |  | Fax: 509-329-2104
dw.nwro@doh.wa.gov |  |  |  |  | SWTR.swro@doh.wa.gov |  |  |  | ero.sw.Treatment.Reports@doh.wa.gov
For Persons with Disabilities
This document is available on request in other formats. To submit a request, please call 1-800-525-0127 (TTY 1-800-833-6388).
DOH Contact
If there are any questions, or if you find any errors in the workbook, please contact:
| Jolyn Leslie, PE |  |  |  |  | Teresa Walker, PE
| Northwest Drinking Water Operations |  |  |  |  | Southwest Drinking Water Operations
253-395-6762 |  | Email: | jolyn.leslie@doh.wa.gov |  |  | 360-236-3032 |  | Email: | teresa.walker@doh.wa.gov
| Nancy Feagin, PE |  |  |  |  | Russell Mau, PE
| Engineering and Technical Services |  |  |  |  | Eastern Drinking Water Operations
253-395-6765 |  | Email: | nancy.feagin@doh.wa.gov |  |  | 509-329-2116 |  | Email: | Russell.Mau@doh.wa.gov
Notes on Version 1.0 Revised 02/14/2006
Overall Log Treatment Required has been set to 3.0 on the SWTR Monthly Disinfection Rept form.
Notes on Version 2.0 Revised 02/05/2015
Incorporated new technology-specific summary form
Changed conditional formatting to eliminate red text (doesn't always come through on a fax machine)
Notes on Version 2.1 revised 11/30/2015
Added two questions regarding validation of on-line turbidimeters - Rapid Rate WTP monthly rept
Added turbidity verification log sheet
Added reference to form 331-173 on lines 17 & 18 - Monthly Summary Form
Added primary turbidity standard expiration date - Monthly Summary Form
Notes on Version 2.2 revised 1/9/2017
Added line-by-line instruction sheet
Added filter media depth - Rapid Rate WTP Monthly Rept Form
Removed 0.1 mg/L lower limit on chlorine residual - SWTR Monthly Disinfection Rept
Notes on Version 2.3 revised 8/20/2018
Updated DOH contact information
Added clarification that continuous individual turbidity data must be recorded at least every 15 minutes
Added optional sheet for recording Individual Filter Turbidity Data
Entered default filtration credit of 2.0 to SWTR Monthly Disinfection Report
Added pop-up note to contact DOH if pH> 9.0 (for instructions on how to calculate CT)
Minor edits to the instruction sheet to improve clarity
Notes on Version 2.3.1 revised 10/16/2018
Corrected error in "failure of continuous monitoring" question at bottom of Rapid Rate WTP Monthly Rep.
Notes on Version 2.3.2 revised 4/4/2019
Inserted missing line of data on Giardia CT lookup table (2˚C, 0.2 mg/L)

## Rapid Rate WTP Monthly Rept
Water Treatment Plant Monthly Report Form
[11 empty] | Month |  | Year
| PWS ID |  |  | PWS Name | [7 empty] | County
| Source ID |  |  | Source Name | [7 empty] | Plant ID
Cells and Columns with Blue Headings are intended for data provided by user
| Water Treated in 1000 gals | Total Hours of Operation | Filter Backwash Total in 1000 gal | Chemicals Used (lbs) | [7 empty] | Turbidity NTU |  | Combined Filter Effluent Turbidity 4 hour sample NTU | [6 empty] | No of Samples > 0.3 NTU | Max CFE Turbidity NTU | % NTU Reduction (See Note 1) | Temp C | pH |  | Total Alkalinity mg/L as CaCO3 |  | Calcium Hardness mg/L as CaCO3 Fin
Remarks
Date |  |  |  | Chlorine | Alum | Polymer | Filter Aid | Soda Ash | Ozone |  |  | Raw | Settled | 1st | 2nd | 3rd | 4th | 5th | 6th | Avg |  |  |  | Raw | Raw | Final | Raw | Fin
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0
Avg
| Total number of CFE samples analyzed for month: N = | [5 empty] | 0 |  | Total number of CFE samples exceeding 0.3 NTU: E = | [5 empty] | 0 |  |  | NOTE 1: Percent turbidity reduction for each day of operation: PTR = [(Raw NTU)-(Avg CFE NTU)]x(100)/(Raw NTU)
Satisfactory turbidity performance is 95% or greater. Performance determination: [1-(E/N)]x100 =
| Number of days CFE exceeded 1.0 NTU this month: | [5 empty] | 0 | [11 empty] | Filter media design specs (in) |  |  |  |  | Anthracite |  | Sand |  | Garnet
| Did the CFE continuous monitoring fail to operate for more than five (5) consecutive days during this month? | [10 empty] | Y/N: |  | -If 'Yes' attach incident report. |  |  |  |  | Date of last filter inspection | [8 empty] | # filters with more than 10 percent media loss
| Did you continuously monitor the effluent turbidity of each individual filter (IFE) & record the values at least every 15 minutes (WAC 246-290-664(3))? | [10 empty] | Y/N: |  | -If 'No' attach incident report.
| Did you complete grab sample verfication of on-line turbidimeters at least once per week (WAC 246-290-638 (4))? | [10 empty] | Y/N: | [6 empty] | Report Submitted By | [6 empty] | Signature

## Filter Turbidities
Individual Filter Effluent Turbidities (NTU)
[5 empty] | Month | 0 | Year | 0
| PWS ID | 0 |  |  |  | PWS Name | 0
| Source ID | 0 |  |  |  | Source Name | 0
| County | 0 |  |  |  | Plant ID | 0
Maximum Value for Each Day1,2
Filter Number
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Comments
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
95th Percentile Turbidity Value (NTU)
Individual Filter Turbidity Optimization Goals:
Filtered water turbidity is less than or equal to 0.10 NTU 95% of the time based on maximum daily values.
Filter-to-waste cycle not terminated until turbidity drops below 0.10 NTU
Filters are backwashed before turbidity breakthrough occurs.
1Use one of the following methods: a) Max. value from the SCADA trend line (preferred); b) Max. value from data logger using 1 minute readings; c) Max. value from data logger using 15 minute readings.
2Do not include data from periods when the filter is not sending water to the clearwell, such as during filter-to-waste.

## Online Turb Verification
Weekly Verification Checks-Online Turbidimeters
PWS Name | 0
PWS ID | 0
WEEK 1 (date): |  | Operator Name: |  |  |  | WEEK 2 (date): |  | Operator Name:
Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action | Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action
Example: IFE-FILTER #1/HACH 1720E | 0.08 | 0.08 | 0.09 | Y | none | Example: CFE/HACH 1720E | 0.13 | 0.14 | 0.05 | N | Recalibrated on-line
|  |  |  | * or 10% for the raw | [5 empty] | * or 10% for the raw
WEEK 3 (date): |  | Operator Name: |  |  |  | WEEK 4 (date): |  | Operator Name:
Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action | Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action
* or 10% for the raw
WEEK 5 (date): |  | Operator Name:
Turbidimeter (location/make/model) | SCADA reading NTU | online meter NTU | grab sample NTU | Results within 0.05 NTU*? Y/N | Follow up action
* or 10% for the raw

## SWTR Monthly Disinfection Rept
Washington State Department of Health
SWTR Disinfection Monthly Report Form
| PWS ID | 0 |  | PWS Name | 0 |  |  |  | Month | 0 | Year | 0
| County | 0 | [5 empty] | Submitted By
| Source ID | 0 |  | Source Name | 0 |  | . | WTPO Cert No
| Plant ID | 0 | [5 empty] | Telephone No
Population Served |  |  |  |  | Min Grab Samples Reqd | 1 | Residuals Normally Measured Continuously Y/N
Overall Log Treatment Req'd |  |  | 3 |  | Filtration Log Removal Credit |  |  | 2 |  | Required Disinfection Log Reduction |  |  |  | 1
Cells and Columns with Blue Headings are intended for data provided by user
|  |  | Inactivation Ratio Determination | [7 empty] | Disinfectant Residual at |  |  | Residual in
Note: For correct results, remember to enter your plant's Filtration Log Removal Credit in cell I9 above | [10 empty] | Distribution Entry Point |  |  | Distribution System
Date | Peak Hour Flow gpm | Water Temp C | pH | Chlorine Residual {C} mg/L | Tank Level ft (must be at least __ ft) | Contact Time {T} minutes | Calculated CT {C*T} | Required CT from Tables* | Inact Ratio {Calc CT/Req'd CT} | No. of Samples Collected "C" if Continuous | Lowest Daily Residual mg/L | Duration less than 0.2mg/L hours | DOH Notified? Name & Time | No of Sites Sampled | Minimum Residual mg/L | No of Samples Residual Not Detected
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | [9 empty] | 0 | # < 0.2 mg/L | # > 4 hrs |  | 0 |  | 0
Count | [8 empty] | 0 |  | 0 | 0
Min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Max | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Avg
| *Adjusted for Log Reduction Required |  |  |  |  | No. Days Inact Ratio < 1 |  | 0
DOH Form 331-440-F (Excel version) |  |  |  | Notes: | [5 empty] | Signature

## Monthly Summary
Surface Water Treatment Plant
Monthly Report Summary Form
PWS ID | 0 |  | Source ID | 0 |  |  | Month | 0 | Year | 0
PWS Name | 0 |  |  | Source Name |  | 0
|  |  |  | Plant ID | 0 |  |  | County | 0
|  | Color code for form information: | WTP Monthly Rept |  | SWTR Monthly Disinfection Rept |  |  | To be supplied by user
Source (Raw) Water | 7. Maximum density of raw water fecal coliform (# organisms/100 ml)
| 8. Number of days raw water turbidity was monitored this month | [8 empty] | 0
| 9. Maximum turbidity of the raw water treated by the plant (NTU) | [8 empty] | 0
10. Number of raw water turbidity measurements taken
Filtration | 11. Hours of operation during reporting month | [8 empty] | 0
| 12. Number of filtered water turbidity measurements taken | [8 empty] | 0
| 13. Turbidity performance limit |  | 0.3 NTU | No. of filtered measurements exceeding monthly performance limit: | [5 empty] | 0
| 14. Maximum allowable turbidity |  | 1.0 NTU | No. of days filtered water turbidity measurements exceeded max allowable limit: | [5 empty] | 0
| 15. Maximum filtered water turbidity (NTU) | [8 empty] | 0
16. Average percent turbidity reduction (daily filtration effectiveness calculations for conventional, direct, and in-line filters)
| 17. Did effluent turbidity of any individual filter exceed 1.0 NTU in consecutive 15 min readings? (If Y use form 331-173) | [7 empty] | Y/N:
| 18. Did effluent turbidity of any individual filter exceed 0.5 NTU in 2 consecutive measurements?(If Y use form 331-173) | [7 empty] | Y/N:
| 19. Was unfiltered water provided to consumers at any time? | [7 empty] | Y/N:
| 20. Primary Coagulant name: |  |  |  |  | Dose (mg/L) | Avg |  | Max
| 21. Was coagulation in use at all times the plant was operating? | [7 empty] | Y/N:
| 22. Approved maximum filtration rate (gpm/sq ft): |  |  |  |  | Maximum operational filtration rate (gpm/sq ft)
23. Maximum flow rate treated (Units of gpm)
Inactivation Ratio | 24. Number of days disinfectant CT was monitored this month | [8 empty] | 0
| 25. Number of days inactivation ratio was below 1.0 | [8 empty] | 0
| 26. Lowest inactivation ratio achieved | [8 empty] | 0
Distribution Entry Point Samples | 27. Number of days during which plant produced water during month | [8 empty] | 0
| 28. Number of entry point residual samples analyzed during month | [8 empty] | 0
| 29. No of days when residual fell below 0.2 mg/l | [8 empty] | 0
| 30. No of days when residual fell below 0.2 mg/l for more than 4 hours | [8 empty] | 0
Distribution System Residuals | 31. Number of days water served to public this month
32. Number of days distribution system disinfectant residual was monitored
| 33. No of distribution system disinfectant residual samples measured this month | [8 empty] | 0
| 34. No of samples where no disinfectant residual was detected | [8 empty] | 0
35. Average of all disinfectant residual measurements taken with coliform samples (mg/L)
Finished Water/ General | 36. Number of water quality complaints received from consumers served by system
| 37. Did certified operator take all req'd pH, temp, turbidity, and residual disinfectant measurements? | [7 empty] | Y/N:
| 38. All turbidimeters calibrated with a primary standard within the last quarter? | [5 empty] | Date: |  | Y/N:
Primary standard expiration date:
| 39. Critical alarms tested? |  | Remarks: |  |  |  | Date: |  | Y/N:
As the responsible operator in charge, I certify that I have reviewed the information submitted on all the monthly operating report forms:
Report Submitted By | [5 empty] | BTO/WTPO Cert No
Signature | [5 empty] | Telephone Number
See Cover Page for information on where to send this form.

## Line-by-Line_Instructions
Line-by-Line Instructions
General Reminder: Cells and columns intended for user input have titles or headings colored blue.
Rapid Rate WTP Monthly Rept
Column | Comment
Water Treated (1000 gal) | Include all water produced by the plant (includes filter-to-waste)
Total Hours of Operation | You can determine this using SCADA, a chart recorder, a plant run time meter, or estimate using the total volume produced divided by the known (fixed) plant flow rate
Filter Backwash (1000 gal)
Chemicals Used (lbs) | (liquid) lbs/day=lbs/gal x gal/day lbs/gal=(% Solution/100) x 8.34 lbs/gal x specific gravity
(liquid mixed from dry) lbs/gal=lbs dry chemical/gallons of solution
Turbidity Raw | If monitoring continuously, record the daily average value. If using grab samples, collect representative sample(s) after startup once the plant is running smoothly. Sample prior to chemical addition. For systems that recycle backwash water to the head of the plant, measure the raw turbidity prior to (upstream from) the recycle point.
Turbidity Settled | Direct filtration plants leave this blank. For plants that monitor continuously, record the daily average value. If using grab samples, collect a representative sample after startup once the plant is running smoothly. If you collect multiple grab samples report the average value.
Combined Filter Effluent Turbidity | For plants that do not operate 24/7, record the first reading within 15 minutes after plant startup, and subsequent readings every four hours as long as the plant continues to run. For plants with multiple startups in a day, repeat this for each startup. Do not record values when the plant is not running.
Max CFE Turbidity | This is the absolute maximum for the day (not the maximum of the four-hour readings). Call your DOH regional office immediately if this exceeds 1.0 NTU
Temp (Raw) | As needed for process control
pH Raw/Final | As needed for process control and/or corrosion control
Alkalinity Raw/Finished | As needed for process control and/or corrosion control. Systems using a coagulant like alum that consumes alkalinity should measure at least weekly
Calcium hardness | As needed for corrosion control
Remarks | Record anything unusual or out-of-the-ordinary here.
Filter Turbidities
Rapid rate filters using direct, in-line or conventional filtration must continuously measure the turbidity from each individual filter and record the results every 15 minutes. You must keep turbidity data for at least 5 years. You may use this optional form to record the daily max individual filter effluent turbidity value for each filter and compare your plant performance against the optimization goals.
Online Turb Verification
This is an optional template for recording the required weekly verification checks of your online turbidimeters. If you already have a system in place to record this information, you do not need to use. Keep this on file. It is not necessary to submit it unless requested by the department.
SWTR Monthly Disinfection Report
Column | Comment
Peak hourly flow (PHF) | This is the maximum one-hour flow through the contact basin, expressed in gallons per minute. It is not the peak instantaneous flow. Use the flow into or out of the contact basin, whichever is higher. For most systems, this is the flow leaving the contact basin.
Water temperature | Measure during PHF at the same location as chlorine residual (for CT). May also report daily minimum if you have continous measurement.
pH | Measure during PHF at the same location as chlorine residual (for CT). May also report daily maximum if you have continuous measurement. Call your DOH regional office for instructions if your pH exceeds 9.0
Chlorine Residual (CT) | Measure the free chlorine residual at the end of the contact basin or pipe, prior to the first customer, during PHF. May also report daily minimum if you have continuous measurement.
Tank Level | If you use a storage tank or clearwell for contact time, record the tank level during peak hourly flow. May also report the daily minimum tank level. In the column header, record the assumed minimum tank level, if any, used for your CT calculation.
Contact Time | Calculate this every day (not at the end of the month). Use PHF and your DOH-approved CT calculation.
Inact Ratio | This calculates automatically based on the numbers you enter. Call your DOH regional office immediately if the value drops below 1.0
Entry Point-Lowest Daily Residual mg/L | Systems serving more than 3300 people must monitor continuously & report the lowest absolute value for the day. If continuous equipment fails, you must take grab samples every four hours and have equipment back up and running with five working days. Systems serving less than 3300 people may use grab samples (1-4 per day depending on population) Systems using grab sampling, take one sample at PHF and the remaining samples spaced over the period that the plant produces water. Record the lowest grab sample result. Call your DOH regional office immediately if this value drops below 0.2 mg/L
Entry Point-Duration less than 0.2 mg/L hours | Enter the total length of time that the residual was below 0.2 mg/L.
DOH Notified? Name & Time | Each day the residual was below 0.2 mg/L write the date and the name of the person you reported to at DOH
Distribution-No of Sites Sampled | Measure distribution residual at least once per day and at the same time and location as coliform samples. Measure from representative locations throughout the distribution system.
Minimum Residual mg/L | Record the lowest free chlorine residual for the day. Systems using chloramines: record the total chlorine residual
No of Samples Residual Not Detected | Systems that use heterotrophic plate counts (HPC): an HPC level less than or equal to 500 organisms/mL is considered to have a detectable residual disinfectant concentration. For systems that do not use HPC, "detectable residual disinfectant concentration" means 0.2 mg/L free chlorine, total chlorine or combined chlorine. The department may approve a written request to use a lower value. At a minimum, the request to use a lower value must identify the instrument used to measure the residual disinfectant concentration and include the manufacturer's documentation on the instrument's accuracy to measure the lower value.
Monthly Summary
All blanks must be completed each month. If a question does not apply to your system, please check the n/a box.
Box # | Comment
7 | Enter the maximum result from all of your fecal coliform samples. You are required to collect fecal coliform samples at a frequency equal to 10% of your number of routine coliform samples, or at least one sample per month. The maximum number of samples is one per day.
9 | Maximum raw water turbidity-Maximum of the reported daily values for the month. (populates automatically)
10 | If raw water turbidity was continuously monitored throughout the month, enter the number of days in the month.
12 | Filtered water turbidity measurements reported for the combined filter effluent from the treatment plant. (populates automatically)
13 & 14 | The turbidity performance limit for rapid rate filtration is "0.3 NTU" and the maximum allowable turbidity is "1.0 NTU".
16 | Average for the month of the daily calculated percent turbidity reduction. Equation=[(R-F)/R]X100%, where R=Raw turbidity and F=Combined filter effluent turbidty. Satisfactory effectiveness is ≥80% for conventional, direct, or in-line filtration. (populates automatically)
17 | If you answered "yes" you must complete Form #331-173 Supplemental Reporting - Individual Filter Turbidity for Conventional, Direct, or In-line Filters and submit it with your other report forms. This also applies to systems with one or two filters and only one finished water turbidimeter.
18 | This question applies only to systems serving 10,000 or more people; smaller systems check the N/A box. Check "yes" if these conditions applied at the end of the first four hours of operation after backwashing filters or taking them off-line. If you answered "yes" you must complete Form #331-173 Supplemental Reporting - Individual Filter Turbidity for Conventional, Direct, or In-line Filters and submit it with your other report forms.
19 | Specifically, was any unfiltered surface water or GWI water provided, not from an alternate source such as wells.
20 | Enter the commonly used name such as "alum" or "ACH/PACL". If you use a polymer, enter the trade name such as "Sumaclear 801B polymer" or "Superfloc C 572 polymer". Use daily averages to calculation avg/max dose.
22 | Enter the maximum filtration rate approved for your plant and the max rate observed during the month. For systems using SCADA this can be based on 15 minute intervals. For filter media specifications, enter the number of inches of each media type from your approved design, the date of the last filter media inspection in which you checked media depth, and the number of filters where the total media depth is currently less than 10 percent below the design specifications.
23 | Maximum flowrate through the filters. This may be different from the peak hourly flow (PHF) on the Disinfection Report.
34 | Disinfectant Residuals - A heterotrophic plate count (HPC) level less than or equal to 500 organisms/mL is considered to have a detectable residual disinfectant concentration.
35 | This question is to help meet a DBP rule requirement: systems must measure and report the average value each month of the residual disinfectant level at the same time/location as coliform samples. Subpart H (surface water) systems have the option of using the results of the daily distribution samples - this option should be specified in your DBP monitoring plan. If you have opted to use the daily distribution samples, enter that average here.
37 | Analytical Measurements - Only qualified persons (such as certified operators) shall conduct measurements for pH, temperature, turbidity, and residual disinfectant concentrations. See WAC 246-290-638(1) for details.
38 | Turbidimeter Calibration - Calibrate turbidity equipment based upon a primary standard on at least a quarterly basis for instruments using an incandescent light source and on at least an annual basis for instruments using an LED or laser light source. If there are more than one and they were calibrated on different dates, enter the earliest calibration date. WAC 246-290-638(4)
39 | Critical alarms are those alarms that monitor a critical treatment process such as filtration or disinfection where treatment failure poses an immediate risk to public health and/or safety. For plants that run in an unattended mode, these alarms must trigger plant shutdown, not just dial out to the on-call operator. Recommended testing frequency: Plants staffed 24/7 (quarterly), Plants that operate some of the time unattended (monthly), Plants with a history of reliability problems (weekly)
40 | The operator in responsible charge with the appropriate level of certification (at or above the plant rating) must sign this form.

## Req'd CT Calc (hidden)
| 0 | 501 | 1001 | 2501 | 3301 |  |  |  | 0 | 6 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5 | 6.6 | 6.7 | 6.8 | 6.9 | 7 | 7.1 | 7.2 | 7.3 | 7.4 | 7.5 | 7.6 | 7.7 | 7.8 | 7.9 | 8 | 8.1 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 8.7 | 8.8 | 8.9 | 9
| 1 | 2 | 3 | 4 | 6 |  |  |  | 2 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
| PopServed | 0 |  |  | MinGrab | 1
|  |  | Inactivation Ratio Determination | [5 empty] | 0 2: Disinfection Log Reduction Req'd; 6.3 5: 1
Date | Peak Hour Flow gpm | Water Temp C | pH | Chlorine Residual {C} mg/L | Contact Time {T} minutes | Calculated CT {C*T} | Required CT from Tables | Inact Ratio {Calc CT/Req'd CT} | 0 2: Temp Adj; 6 2: pH Offset; 6.1 3: Chlorine Adj; 6.2 4: CT; 6.3 5: CT Calc; 6.4 6: Table Lookup; 6.5 7: CT Required; 6.6 8: Inact Ratio; 6.8 10: Lowest Daily Residual mg/L; 6.9 11: Duration less than 0.2mg/L hours; 7 12: Valid Durations hours
1 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
2 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
3 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
4 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
5 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
6 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
7 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
8 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
9 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
10 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
11 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
12 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
13 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
14 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
15 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
16 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
17 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
18 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
19 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
20 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
21 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
22 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
23 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
24 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
25 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
26 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
27 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
28 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
29 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
30 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
31 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
Total
Count | [8 empty] | 7 12: 0
Min | [8 empty] | 6.8 10: 0; 6.9 11: 0; 7 12: 0
Max | [8 empty] | 6.8 10: 0; 6.9 11: 0; 7 12: 0
Avg
| ADAM | 3
| ASOT | 3
| BENT | 3
| CHEL | 3
| CLAL | 2
| CLAR | 2
| CLIC | 3
| COLO | 3
| COLU | 3
| COWL | 2
| DOUG | 3
| FERR | 3
| FRAN | 3
| GARF | 3
| GRAN | 3
| GRAY | 2
| ILAN | 1
| ISLA | 1
| JEFF | 2
| KING | 1
| KITI | 3
| KITS | 2
| KITT | 3
| KLIC | 3
| KOWL | 2
| LEWI | 2
| LINC | 3
| MASI | 2
| MASO | 2
| OKAN | 3
| OKON | 3
| PACI | 2
| PEIR | 1
| PEND | 3
| PIER | 1
| POND | 3
| SAN | 1
| SANJ | 1
| SKAG | 1
| SKAM | 2
| SNOH | 1
| SPOK | 3
| STEV | 3
| THUR | 2
| TURS | 2
| WALL | 3
| WATC | 1
| WHAT | 1
| WHIT | 3
| WITM | 3
| YAKA | 3
| YAKI | 3

## CT Lookup Table (hidden)
Look-up Table for Required CT for 1 log Reduction in Giardia at Various Temperatures, Chlorine Concentration and pH
Temp | Chlorine | Lookup | [6 empty] | pH | [17 empty] | pH
Degrees | Conc | Row
C | (mg/l) |  | 6 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5 | 6.6 | 6.7 | 6.8 | 6.9 | 7 | 7.1 | 7.2 | 7.3 | 7.4 | 7.5 | 7.6 | 7.7 | 7.8 | 7.9 | 8 | 8.1 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 8.7 | 8.8 | 8.9 | 9
0 | 0 | 0 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0 | 500 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0.2 | 502 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0.4 | 504 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0.6 | 506 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.6 | 72.2 | 74.8 | 77.4 | 80 | 83 | 86 | 89 | 92 | 95 | 98.8 | 102.6 | 106.4 | 110.2 | 114 | 118.4 | 122.8 | 127.2 | 131.6 | 136
0.5 | 0.8 | 508 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.8 | 73.6 | 76.4 | 79.2 | 82 | 85.2 | 88.4 | 91.6 | 94.8 | 98 | 102 | 106 | 110 | 114 | 118 | 122.6 | 127.2 | 131.8 | 136.4 | 141
0.5 | 1 | 510 | 49 | 51 | 53 | 55 | 57 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.4 | 90.8 | 94.2 | 97.6 | 101 | 105.2 | 109.4 | 113.6 | 117.8 | 122 | 126.8 | 131.6 | 136.4 | 141.2 | 146
0.5 | 1.2 | 512 | 51 | 52.8 | 54.6 | 56.4 | 58.2 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86 | 89.6 | 93.2 | 96.8 | 100.4 | 104 | 108.2 | 112.4 | 116.6 | 120.8 | 125 | 130 | 135 | 140 | 145 | 150
0.5 | 1.4 | 514 | 52 | 53.8 | 55.6 | 57.4 | 59.2 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.6 | 96.2 | 99.8 | 103.4 | 107 | 111.4 | 115.8 | 120.2 | 124.6 | 129 | 134.2 | 139.4 | 144.6 | 149.8 | 155
0.5 | 1.6 | 516 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63 | 65.4 | 67.8 | 70.2 | 72.6 | 75 | 78.2 | 81.4 | 84.6 | 87.8 | 91 | 94.8 | 98.6 | 102.4 | 106.2 | 110 | 114.4 | 118.8 | 123.2 | 127.6 | 132 | 137.4 | 142.8 | 148.2 | 153.6 | 159
0.5 | 1.8 | 518 | 54 | 56 | 58 | 60 | 62 | 64 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 80.2 | 83.4 | 86.6 | 89.8 | 93 | 97 | 101 | 105 | 109 | 113 | 117.6 | 122.2 | 126.8 | 131.4 | 136 | 141.4 | 146.8 | 152.2 | 157.6 | 163
0.5 | 2 | 520 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 82.2 | 85.4 | 88.6 | 91.8 | 95 | 99 | 103 | 107 | 111 | 115 | 119.8 | 124.6 | 129.4 | 134.2 | 139 | 144.6 | 150.2 | 155.8 | 161.4 | 167
0.5 | 2.2 | 522 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.6 | 88.2 | 91.8 | 95.4 | 99 | 102.8 | 106.6 | 110.4 | 114.2 | 118 | 122.8 | 127.6 | 132.4 | 137.2 | 142 | 147.6 | 153.2 | 158.8 | 164.4 | 170
0.5 | 2.4 | 524 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.8 | 73.6 | 76.4 | 79.2 | 82 | 85.4 | 88.8 | 92.2 | 95.6 | 99 | 103.2 | 107.4 | 111.6 | 115.8 | 120 | 125 | 130 | 135 | 140 | 145 | 150.8 | 156.6 | 162.4 | 168.2 | 174
0.5 | 2.6 | 526 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.4 | 90.8 | 94.2 | 97.6 | 101 | 105.4 | 109.8 | 114.2 | 118.6 | 123 | 128 | 133 | 138 | 143 | 148 | 154 | 160 | 166 | 172 | 178
0.5 | 2.8 | 528 | 59 | 61.4 | 63.8 | 66.2 | 68.6 | 71 | 74 | 77 | 80 | 83 | 86 | 89.4 | 92.8 | 96.2 | 99.6 | 103 | 107.4 | 111.8 | 116.2 | 120.6 | 125 | 130.2 | 135.4 | 140.6 | 145.8 | 151 | 157 | 163 | 169 | 175 | 181
0.5 | 3 | 530 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 75 | 78 | 81 | 84 | 87 | 90.6 | 94.2 | 97.8 | 101.4 | 105 | 109.4 | 113.8 | 118.2 | 122.6 | 127 | 132.2 | 137.4 | 142.6 | 147.8 | 153 | 159.2 | 165.4 | 171.6 | 177.8 | 184
1 | 0 | 1000 | 44.4444 | 46.0222 | 47.6 | 49.1778 | 50.7556 | 52.3333 | 54.4444 | 56.5556 | 58.6667 | 60.7778 | 62.8889 | 65.5778 | 68.2667 | 70.9556 | 73.6444 | 76.3333 | 78.8889 | 81.4444 | 84 | 86.5556 | 89.1111 | 92.6 | 96.0889 | 99.5778 | 103.0667 | 106.5556 | 110.4222 | 114.2889 | 118.1556 | 122.0222 | 125.8889
1 | 0.2 | 1002 | 44.4444 | 46.0222 | 47.6 | 49.1778 | 50.7556 | 52.3333 | 54.4444 | 56.5556 | 58.6667 | 60.7778 | 62.8889 | 65.5778 | 68.2667 | 70.9556 | 73.6444 | 76.3333 | 78.8889 | 81.4444 | 84 | 86.5556 | 89.1111 | 92.6 | 96.0889 | 99.5778 | 103.0667 | 106.5556 | 110.4222 | 114.2889 | 118.1556 | 122.0222 | 125.8889
1 | 0.4 | 1004 | 44.4444 | 46.0222 | 47.6 | 49.1778 | 50.7556 | 52.3333 | 54.4444 | 56.5556 | 58.6667 | 60.7778 | 62.8889 | 65.5778 | 68.2667 | 70.9556 | 73.6444 | 76.3333 | 78.8889 | 81.4444 | 84 | 86.5556 | 89.1111 | 92.6 | 96.0889 | 99.5778 | 103.0667 | 106.5556 | 110.4222 | 114.2889 | 118.1556 | 122.0222 | 125.8889
1 | 0.6 | 1006 | 45.4444 | 47.2 | 48.9556 | 50.7111 | 52.4667 | 54.2222 | 56.3556 | 58.4889 | 60.6222 | 62.7556 | 64.8889 | 67.4 | 69.9111 | 72.4222 | 74.9333 | 77.4444 | 80.3556 | 83.2667 | 86.1778 | 89.0889 | 92 | 95.6667 | 99.3333 | 103 | 106.6667 | 110.3333 | 114.6 | 118.8667 | 123.1333 | 127.4 | 131.6667
1 | 0.8 | 1008 | 46.4444 | 48.2 | 49.9556 | 51.7111 | 53.4667 | 55.2222 | 57.3556 | 59.4889 | 61.6222 | 63.7556 | 65.8889 | 68.5778 | 71.2667 | 73.9556 | 76.6444 | 79.3333 | 82.4444 | 85.5556 | 88.6667 | 91.7778 | 94.8889 | 98.7556 | 102.6222 | 106.4889 | 110.3556 | 114.2222 | 118.6667 | 123.1111 | 127.5556 | 132 | 136.4444
1 | 1 | 1010 | 47.4444 | 49.3778 | 51.3111 | 53.2444 | 55.1778 | 57.1111 | 59.2444 | 61.3778 | 63.5111 | 65.6444 | 67.7778 | 70.4889 | 73.2 | 75.9111 | 78.6222 | 81.3333 | 84.6222 | 87.9111 | 91.2 | 94.4889 | 97.7778 | 101.8444 | 105.9111 | 109.9778 | 114.0444 | 118.1111 | 122.7556 | 127.4 | 132.0444 | 136.6889 | 141.3333
1 | 1.2 | 1012 | 49.3333 | 51.0667 | 52.8 | 54.5333 | 56.2667 | 58 | 60.3333 | 62.6667 | 65 | 67.3333 | 69.6667 | 72.3778 | 75.0889 | 77.8 | 80.5111 | 83.2222 | 86.7111 | 90.2 | 93.6889 | 97.1778 | 100.6667 | 104.7333 | 108.8 | 112.8667 | 116.9333 | 121 | 125.8444 | 130.6889 | 135.5333 | 140.3778 | 145.2222
1 | 1.4 | 1014 | 50.2222 | 51.9778 | 53.7333 | 55.4889 | 57.2444 | 59 | 61.5111 | 64.0222 | 66.5333 | 69.0444 | 71.5556 | 74.4444 | 77.3333 | 80.2222 | 83.1111 | 86 | 89.5111 | 93.0222 | 96.5333 | 100.0444 | 103.5556 | 107.8 | 112.0444 | 116.2889 | 120.5333 | 124.7778 | 129.8222 | 134.8667 | 139.9111 | 144.9556 | 150
1 | 1.6 | 1016 | 50.3333 | 52.4444 | 54.5556 | 56.6667 | 58.7778 | 60.8889 | 63.2222 | 65.5556 | 67.8889 | 70.2222 | 72.5556 | 75.6444 | 78.7333 | 81.8222 | 84.9111 | 88 | 91.6667 | 95.3333 | 99 | 102.6667 | 106.3333 | 110.6222 | 114.9111 | 119.2 | 123.4889 | 127.7778 | 132.9778 | 138.1778 | 143.3778 | 148.5778 | 153.7778
1 | 1.8 | 1018 | 52.2222 | 54.1556 | 56.0889 | 58.0222 | 59.9556 | 61.8889 | 64.4 | 66.9111 | 69.4222 | 71.9333 | 74.4444 | 77.5333 | 80.6222 | 83.7111 | 86.8 | 89.8889 | 93.7556 | 97.6222 | 101.4889 | 105.3556 | 109.2222 | 113.6889 | 118.1556 | 122.6222 | 127.0889 | 131.5556 | 136.7778 | 142 | 147.2222 | 152.4444 | 157.6667
1 | 2 | 1020 | 53.2222 | 55.3333 | 57.4444 | 59.5556 | 61.6667 | 63.7778 | 66.2889 | 68.8 | 71.3111 | 73.8222 | 76.3333 | 79.4444 | 82.5556 | 85.6667 | 88.7778 | 91.8889 | 95.7556 | 99.6222 | 103.4889 | 107.3556 | 111.2222 | 115.8667 | 120.5111 | 125.1556 | 129.8 | 134.4444 | 139.8667 | 145.2889 | 150.7111 | 156.1333 | 161.5556
1 | 2.2 | 1022 | 54.1111 | 56.2444 | 58.3778 | 60.5111 | 62.6444 | 64.7778 | 67.4667 | 70.1556 | 72.8444 | 75.5333 | 78.2222 | 81.6889 | 85.1556 | 88.6222 | 92.0889 | 95.5556 | 99.2667 | 102.9778 | 106.6889 | 110.4 | 114.1111 | 118.7556 | 123.4 | 128.0444 | 132.6889 | 137.3333 | 142.7556 | 148.1778 | 153.6 | 159.0222 | 164.4444
1 | 2.4 | 1024 | 55.1111 | 57.2444 | 59.3778 | 61.5111 | 63.6444 | 65.7778 | 68.4667 | 71.1556 | 73.8444 | 76.5333 | 79.2222 | 82.5333 | 85.8444 | 89.1556 | 92.4667 | 95.7778 | 99.8222 | 103.8667 | 107.9111 | 111.9556 | 116 | 120.8444 | 125.6889 | 130.5333 | 135.3778 | 140.2222 | 145.8444 | 151.4667 | 157.0889 | 162.7111 | 168.3333
1 | 2.6 | 1026 | 56.1111 | 58.4222 | 60.7333 | 63.0444 | 65.3556 | 67.6667 | 70.3556 | 73.0444 | 75.7333 | 78.4222 | 81.1111 | 84.4222 | 87.7333 | 91.0444 | 94.3556 | 97.6667 | 101.9111 | 106.1556 | 110.4 | 114.6444 | 118.8889 | 123.7333 | 128.5778 | 133.4222 | 138.2667 | 143.1111 | 148.9111 | 154.7111 | 160.5111 | 166.3111 | 172.1111
1 | 2.8 | 1028 | 57 | 59.3111 | 61.6222 | 63.9333 | 66.2444 | 68.5556 | 71.4444 | 74.3333 | 77.2222 | 80.1111 | 83 | 86.3111 | 89.6222 | 92.9333 | 96.2444 | 99.5556 | 103.8222 | 108.0889 | 112.3556 | 116.6222 | 120.8889 | 125.9111 | 130.9333 | 135.9556 | 140.9778 | 146 | 151.8 | 157.6 | 163.4 | 169.2 | 175
1 | 3 | 1030 | 58 | 60.3111 | 62.6222 | 64.9333 | 67.2444 | 69.5556 | 72.4667 | 75.3778 | 78.2889 | 81.2 | 84.1111 | 87.6 | 91.0889 | 94.5778 | 98.0667 | 101.5556 | 105.8 | 110.0444 | 114.2889 | 118.5333 | 122.7778 | 127.8222 | 132.8667 | 137.9111 | 142.9556 | 148 | 154 | 160 | 166 | 172 | 178
2 | 0 | 2000 | 41.3333 | 42.8667 | 44.4 | 45.9333 | 47.4667 | 49 | 50.9333 | 52.8667 | 54.8 | 56.7333 | 58.6667 | 61.1333 | 63.6 | 66.0667 | 68.5333 | 71 | 73.4667 | 75.9333 | 78.4 | 80.8667 | 83.3333 | 86.6 | 89.8667 | 93.1333 | 96.4 | 99.6667 | 103.2667 | 106.8667 | 110.4667 | 114.0667 | 117.6667
2 | 0.2 | 2002 | 41.3333 | 42.8667 | 44.4 | 45.9333 | 47.4667 | 49 | 50.9333 | 52.8667 | 54.8 | 56.7333 | 58.6667 | 61.1333 | 63.6 | 66.0667 | 68.5333 | 71 | 73.4667 | 75.9333 | 78.4 | 80.8667 | 83.3333 | 86.6 | 89.8667 | 93.1333 | 96.4 | 99.6667 | 103.2667 | 106.8667 | 110.4667 | 114.0667 | 117.6667
2 | 0.4 | 2004 | 41.3333 | 42.8667 | 44.4 | 45.9333 | 47.4667 | 49 | 50.9333 | 52.8667 | 54.8 | 56.7333 | 58.6667 | 61.1333 | 63.6 | 66.0667 | 68.5333 | 71 | 73.4667 | 75.9333 | 78.4 | 80.8667 | 83.3333 | 86.6 | 89.8667 | 93.1333 | 96.4 | 99.6667 | 103.2667 | 106.8667 | 110.4667 | 114.0667 | 117.6667
2 | 0.6 | 2006 | 42.3333 | 44 | 45.6667 | 47.3333 | 49 | 50.6667 | 52.6667 | 54.6667 | 56.6667 | 58.6667 | 60.6667 | 63 | 65.3333 | 67.6667 | 70 | 72.3333 | 75.0667 | 77.8 | 80.5333 | 83.2667 | 86 | 89.4 | 92.8 | 96.2 | 99.6 | 103 | 107 | 111 | 115 | 119 | 123
2 | 0.8 | 2008 | 43.3333 | 45 | 46.6667 | 48.3333 | 50 | 51.6667 | 53.6667 | 55.6667 | 57.6667 | 59.6667 | 61.6667 | 64.1333 | 66.6 | 69.0667 | 71.5333 | 74 | 76.9333 | 79.8667 | 82.8 | 85.7333 | 88.6667 | 92.2667 | 95.8667 | 99.4667 | 103.0667 | 106.6667 | 110.8 | 114.9333 | 119.0667 | 123.2 | 127.3333
2 | 1 | 2010 | 44.3333 | 46.1333 | 47.9333 | 49.7333 | 51.5333 | 53.3333 | 55.3333 | 57.3333 | 59.3333 | 61.3333 | 63.3333 | 65.8667 | 68.4 | 70.9333 | 73.4667 | 76 | 79.0667 | 82.1333 | 85.2 | 88.2667 | 91.3333 | 95.1333 | 98.9333 | 102.7333 | 106.5333 | 110.3333 | 114.6667 | 119 | 123.3333 | 127.6667 | 132
2 | 1.2 | 2012 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.5333 | 70.0667 | 72.6 | 75.1333 | 77.6667 | 80.9333 | 84.2 | 87.4667 | 90.7333 | 94 | 97.8 | 101.6 | 105.4 | 109.2 | 113 | 117.5333 | 122.0667 | 126.6 | 131.1333 | 135.6667
2 | 1.4 | 2014 | 46.6667 | 48.3333 | 50 | 51.6667 | 53.3333 | 55 | 57.3333 | 59.6667 | 62 | 64.3333 | 66.6667 | 69.3333 | 72 | 74.6667 | 77.3333 | 80 | 83.3333 | 86.6667 | 90 | 93.3333 | 96.6667 | 100.6 | 104.5333 | 108.4667 | 112.4 | 116.3333 | 121.0667 | 125.8 | 130.5333 | 135.2667 | 140
2 | 1.6 | 2016 | 47 | 48.9333 | 50.8667 | 52.8 | 54.7333 | 56.6667 | 58.8667 | 61.0667 | 63.2667 | 65.4667 | 67.6667 | 70.5333 | 73.4 | 76.2667 | 79.1333 | 82 | 85.4 | 88.8 | 92.2 | 95.6 | 99 | 103.0667 | 107.1333 | 111.2 | 115.2667 | 119.3333 | 124.1333 | 128.9333 | 133.7333 | 138.5333 | 143.3333
2 | 1.8 | 2018 | 48.6667 | 50.4667 | 52.2667 | 54.0667 | 55.8667 | 57.6667 | 60 | 62.3333 | 64.6667 | 67 | 69.3333 | 72.2 | 75.0667 | 77.9333 | 80.8 | 83.6667 | 87.2667 | 90.8667 | 94.4667 | 98.0667 | 101.6667 | 105.8667 | 110.0667 | 114.2667 | 118.4667 | 122.6667 | 127.5333 | 132.4 | 137.2667 | 142.1333 | 147
2 | 2 | 2020 | 49.6667 | 51.6 | 53.5333 | 55.4667 | 57.4 | 59.3333 | 61.6667 | 64 | 66.3333 | 68.6667 | 71 | 73.9333 | 76.8667 | 79.8 | 82.7333 | 85.6667 | 89.2667 | 92.8667 | 96.4667 | 100.0667 | 103.6667 | 108 | 112.3333 | 116.6667 | 121 | 125.3333 | 130.4 | 135.4667 | 140.5333 | 145.6 | 150.6667
2 | 2.2 | 2022 | 50.3333 | 52.3333 | 54.3333 | 56.3333 | 58.3333 | 60.3333 | 62.8 | 65.2667 | 67.7333 | 70.2 | 72.6667 | 75.8667 | 79.0667 | 82.2667 | 85.4667 | 88.6667 | 92.2 | 95.7333 | 99.2667 | 102.8 | 106.3333 | 110.6667 | 115 | 119.3333 | 123.6667 | 128 | 133.0667 | 138.1333 | 143.2 | 148.2667 | 153.3333
2 | 2.4 | 2024 | 51.3333 | 53.3333 | 55.3333 | 57.3333 | 59.3333 | 61.3333 | 63.8 | 66.2667 | 68.7333 | 71.2 | 73.6667 | 76.8 | 79.9333 | 83.0667 | 86.2 | 89.3333 | 93.0667 | 96.8 | 100.5333 | 104.2667 | 108 | 112.5333 | 117.0667 | 121.6 | 126.1333 | 130.6667 | 135.9333 | 141.2 | 146.4667 | 151.7333 | 157
2 | 2.6 | 2026 | 52.3333 | 54.4667 | 56.6 | 58.7333 | 60.8667 | 63 | 65.4667 | 67.9333 | 70.4 | 72.8667 | 75.3333 | 78.4667 | 81.6 | 84.7333 | 87.8667 | 91 | 94.9333 | 98.8667 | 102.8 | 106.7333 | 110.6667 | 115.2 | 119.7333 | 124.2667 | 128.8 | 133.3333 | 138.7333 | 144.1333 | 149.5333 | 154.9333 | 160.3333
2 | 2.8 | 2028 | 53 | 55.1333 | 57.2667 | 59.4 | 61.5333 | 63.6667 | 66.3333 | 69 | 71.6667 | 74.3333 | 77 | 80.1333 | 83.2667 | 86.4 | 89.5333 | 92.6667 | 96.6667 | 100.6667 | 104.6667 | 108.6667 | 112.6667 | 117.3333 | 122 | 126.6667 | 131.3333 | 136 | 141.4 | 146.8 | 152.2 | 157.6 | 163
2 | 3 | 2030 | 54 | 56.1333 | 58.2667 | 60.4 | 62.5333 | 64.6667 | 67.4 | 70.1333 | 72.8667 | 75.6 | 78.3333 | 81.6 | 84.8667 | 88.1333 | 91.4 | 94.6667 | 98.6 | 102.5333 | 106.4667 | 110.4 | 114.3333 | 119.0667 | 123.8 | 128.5333 | 133.2667 | 138 | 143.6 | 149.2 | 154.8 | 160.4 | 166
3 | 0 | 3000 | 38.2222 | 39.7111 | 41.2 | 42.6889 | 44.1778 | 45.6667 | 47.4222 | 49.1778 | 50.9333 | 52.6889 | 54.4444 | 56.6889 | 58.9333 | 61.1778 | 63.4222 | 65.6667 | 68.0444 | 70.4222 | 72.8 | 75.1778 | 77.5556 | 80.6 | 83.6444 | 86.6889 | 89.7333 | 92.7778 | 96.1111 | 99.4444 | 102.7778 | 106.1111 | 109.4444
3 | 0.2 | 3002 | 38.2222 | 39.7111 | 41.2 | 42.6889 | 44.1778 | 45.6667 | 47.4222 | 49.1778 | 50.9333 | 52.6889 | 54.4444 | 56.6889 | 58.9333 | 61.1778 | 63.4222 | 65.6667 | 68.0444 | 70.4222 | 72.8 | 75.1778 | 77.5556 | 80.6 | 83.6444 | 86.6889 | 89.7333 | 92.7778 | 96.1111 | 99.4444 | 102.7778 | 106.1111 | 109.4444
3 | 0.4 | 3004 | 38.2222 | 39.7111 | 41.2 | 42.6889 | 44.1778 | 45.6667 | 47.4222 | 49.1778 | 50.9333 | 52.6889 | 54.4444 | 56.6889 | 58.9333 | 61.1778 | 63.4222 | 65.6667 | 68.0444 | 70.4222 | 72.8 | 75.1778 | 77.5556 | 80.6 | 83.6444 | 86.6889 | 89.7333 | 92.7778 | 96.1111 | 99.4444 | 102.7778 | 106.1111 | 109.4444
3 | 0.6 | 3006 | 39.2222 | 40.8 | 42.3778 | 43.9556 | 45.5333 | 47.1111 | 48.9778 | 50.8444 | 52.7111 | 54.5778 | 56.4444 | 58.6 | 60.7556 | 62.9111 | 65.0667 | 67.2222 | 69.7778 | 72.3333 | 74.8889 | 77.4444 | 80 | 83.1333 | 86.2667 | 89.4 | 92.5333 | 95.6667 | 99.4 | 103.1333 | 106.8667 | 110.6 | 114.3333
3 | 0.8 | 3008 | 40.2222 | 41.8 | 43.3778 | 44.9556 | 46.5333 | 48.1111 | 49.9778 | 51.8444 | 53.7111 | 55.5778 | 57.4444 | 59.6889 | 61.9333 | 64.1778 | 66.4222 | 68.6667 | 71.4222 | 74.1778 | 76.9333 | 79.6889 | 82.4444 | 85.7778 | 89.1111 | 92.4444 | 95.7778 | 99.1111 | 102.9333 | 106.7556 | 110.5778 | 114.4 | 118.2222
3 | 1 | 3010 | 41.2222 | 42.8889 | 44.5556 | 46.2222 | 47.8889 | 49.5556 | 51.4222 | 53.2889 | 55.1556 | 57.0222 | 58.8889 | 61.2444 | 63.6 | 65.9556 | 68.3111 | 70.6667 | 73.5111 | 76.3556 | 79.2 | 82.0444 | 84.8889 | 88.4222 | 91.9556 | 95.4889 | 99.0222 | 102.5556 | 106.5778 | 110.6 | 114.6222 | 118.6444 | 122.6667
3 | 1.2 | 3012 | 42.6667 | 44.1333 | 45.6 | 47.0667 | 48.5333 | 50 | 52.0667 | 54.1333 | 56.2 | 58.2667 | 60.3333 | 62.6889 | 65.0444 | 67.4 | 69.7556 | 72.1111 | 75.1556 | 78.2 | 81.2444 | 84.2889 | 87.3333 | 90.8667 | 94.4 | 97.9333 | 101.4667 | 105 | 109.2222 | 113.4444 | 117.6667 | 121.8889 | 126.1111
3 | 1.4 | 3014 | 43.1111 | 44.6889 | 46.2667 | 47.8444 | 49.4222 | 51 | 53.1556 | 55.3111 | 57.4667 | 59.6222 | 61.7778 | 64.2222 | 66.6667 | 69.1111 | 71.5556 | 74 | 77.1556 | 80.3111 | 83.4667 | 86.6222 | 89.7778 | 93.4 | 97.0222 | 100.6444 | 104.2667 | 107.8889 | 112.3111 | 116.7333 | 121.1556 | 125.5778 | 130
3 | 1.6 | 3016 | 43.6667 | 45.4222 | 47.1778 | 48.9333 | 50.6889 | 52.4444 | 54.5111 | 56.5778 | 58.6444 | 60.7111 | 62.7778 | 65.4222 | 68.0667 | 70.7111 | 73.3556 | 76 | 79.1333 | 82.2667 | 85.4 | 88.5333 | 91.6667 | 95.5111 | 99.3556 | 103.2 | 107.0444 | 110.8889 | 115.2889 | 119.6889 | 124.0889 | 128.4889 | 132.8889
3 | 1.8 | 3018 | 45.1111 | 46.7778 | 48.4444 | 50.1111 | 51.7778 | 53.4444 | 55.6 | 57.7556 | 59.9111 | 62.0667 | 64.2222 | 66.8667 | 69.5111 | 72.1556 | 74.8 | 77.4444 | 80.7778 | 84.1111 | 87.4444 | 90.7778 | 94.1111 | 98.0444 | 101.9778 | 105.9111 | 109.8444 | 113.7778 | 118.2889 | 122.8 | 127.3111 | 131.8222 | 136.3333
3 | 2 | 3020 | 46.1111 | 47.8667 | 49.6222 | 51.3778 | 53.1333 | 54.8889 | 57.0444 | 59.2 | 61.3556 | 63.5111 | 65.6667 | 68.4222 | 71.1778 | 73.9333 | 76.6889 | 79.4444 | 82.7778 | 86.1111 | 89.4444 | 92.7778 | 96.1111 | 100.1333 | 104.1556 | 108.1778 | 112.2 | 116.2222 | 120.9333 | 125.6444 | 130.3556 | 135.0667 | 139.7778
3 | 2.2 | 3022 | 46.5556 | 48.4222 | 50.2889 | 52.1556 | 54.0222 | 55.8889 | 58.1333 | 60.3778 | 62.6222 | 64.8667 | 67.1111 | 70.0444 | 72.9778 | 75.9111 | 78.8444 | 81.7778 | 85.1333 | 88.4889 | 91.8444 | 95.2 | 98.5556 | 102.5778 | 106.6 | 110.6222 | 114.6444 | 118.6667 | 123.3778 | 128.0889 | 132.8 | 137.5111 | 142.2222
3 | 2.4 | 3024 | 47.5556 | 49.4222 | 51.2889 | 53.1556 | 55.0222 | 56.8889 | 59.1333 | 61.3778 | 63.6222 | 65.8667 | 68.1111 | 71.0667 | 74.0222 | 76.9778 | 79.9333 | 82.8889 | 86.3111 | 89.7333 | 93.1556 | 96.5778 | 100 | 104.2222 | 108.4444 | 112.6667 | 116.8889 | 121.1111 | 126.0222 | 130.9333 | 135.8444 | 140.7556 | 145.6667
3 | 2.6 | 3026 | 48.5556 | 50.5111 | 52.4667 | 54.4222 | 56.3778 | 58.3333 | 60.5778 | 62.8222 | 65.0667 | 67.3111 | 69.5556 | 72.5111 | 75.4667 | 78.4222 | 81.3778 | 84.3333 | 87.9556 | 91.5778 | 95.2 | 98.8222 | 102.4444 | 106.6667 | 110.8889 | 115.1111 | 119.3333 | 123.5556 | 128.5556 | 133.5556 | 138.5556 | 143.5556 | 148.5556
3 | 2.8 | 3028 | 49 | 50.9556 | 52.9111 | 54.8667 | 56.8222 | 58.7778 | 61.2222 | 63.6667 | 66.1111 | 68.5556 | 71 | 73.9556 | 76.9111 | 79.8667 | 82.8222 | 85.7778 | 89.5111 | 93.2444 | 96.9778 | 100.7111 | 104.4444 | 108.7556 | 113.0667 | 117.3778 | 121.6889 | 126 | 131 | 136 | 141 | 146 | 151
3 | 3 | 3030 | 50 | 51.9556 | 53.9111 | 55.8667 | 57.8222 | 59.7778 | 62.3333 | 64.8889 | 67.4444 | 70 | 72.5556 | 75.6 | 78.6444 | 81.6889 | 84.7333 | 87.7778 | 91.4 | 95.0222 | 98.6444 | 102.2667 | 105.8889 | 110.3111 | 114.7333 | 119.1556 | 123.5778 | 128 | 133.2 | 138.4 | 143.6 | 148.8 | 154
4 | 0 | 4000 | 35.1111 | 36.5556 | 38 | 39.4444 | 40.8889 | 42.3333 | 43.9111 | 45.4889 | 47.0667 | 48.6444 | 50.2222 | 52.2444 | 54.2667 | 56.2889 | 58.3111 | 60.3333 | 62.6222 | 64.9111 | 67.2 | 69.4889 | 71.7778 | 74.6 | 77.4222 | 80.2444 | 83.0667 | 85.8889 | 88.9556 | 92.0222 | 95.0889 | 98.1556 | 101.2222
4 | 0.2 | 4002 | 35.1111 | 36.5556 | 38 | 39.4444 | 40.8889 | 42.3333 | 43.9111 | 45.4889 | 47.0667 | 48.6444 | 50.2222 | 52.2444 | 54.2667 | 56.2889 | 58.3111 | 60.3333 | 62.6222 | 64.9111 | 67.2 | 69.4889 | 71.7778 | 74.6 | 77.4222 | 80.2444 | 83.0667 | 85.8889 | 88.9556 | 92.0222 | 95.0889 | 98.1556 | 101.2222
4 | 0.4 | 4004 | 35.1111 | 36.5556 | 38 | 39.4444 | 40.8889 | 42.3333 | 43.9111 | 45.4889 | 47.0667 | 48.6444 | 50.2222 | 52.2444 | 54.2667 | 56.2889 | 58.3111 | 60.3333 | 62.6222 | 64.9111 | 67.2 | 69.4889 | 71.7778 | 74.6 | 77.4222 | 80.2444 | 83.0667 | 85.8889 | 88.9556 | 92.0222 | 95.0889 | 98.1556 | 101.2222
4 | 0.6 | 4006 | 36.1111 | 37.6 | 39.0889 | 40.5778 | 42.0667 | 43.5556 | 45.2889 | 47.0222 | 48.7556 | 50.4889 | 52.2222 | 54.2 | 56.1778 | 58.1556 | 60.1333 | 62.1111 | 64.4889 | 66.8667 | 69.2444 | 71.6222 | 74 | 76.8667 | 79.7333 | 82.6 | 85.4667 | 88.3333 | 91.8 | 95.2667 | 98.7333 | 102.2 | 105.6667
4 | 0.8 | 4008 | 37.1111 | 38.6 | 40.0889 | 41.5778 | 43.0667 | 44.5556 | 46.2889 | 48.0222 | 49.7556 | 51.4889 | 53.2222 | 55.2444 | 57.2667 | 59.2889 | 61.3111 | 63.3333 | 65.9111 | 68.4889 | 71.0667 | 73.6444 | 76.2222 | 79.2889 | 82.3556 | 85.4222 | 88.4889 | 91.5556 | 95.0667 | 98.5778 | 102.0889 | 105.6 | 109.1111
4 | 1 | 4010 | 38.1111 | 39.6444 | 41.1778 | 42.7111 | 44.2444 | 45.7778 | 47.5111 | 49.2444 | 50.9778 | 52.7111 | 54.4444 | 56.6222 | 58.8 | 60.9778 | 63.1556 | 65.3333 | 67.9556 | 70.5778 | 73.2 | 75.8222 | 78.4444 | 81.7111 | 84.9778 | 88.2444 | 91.5111 | 94.7778 | 98.4889 | 102.2 | 105.9111 | 109.6222 | 113.3333
4 | 1.2 | 4012 | 39.3333 | 40.6667 | 42 | 43.3333 | 44.6667 | 46 | 47.9333 | 49.8667 | 51.8 | 53.7333 | 55.6667 | 57.8444 | 60.0222 | 62.2 | 64.3778 | 66.5556 | 69.3778 | 72.2 | 75.0222 | 77.8444 | 80.6667 | 83.9333 | 87.2 | 90.4667 | 93.7333 | 97 | 100.9111 | 104.8222 | 108.7333 | 112.6444 | 116.5556
4 | 1.4 | 4014 | 39.5556 | 41.0444 | 42.5333 | 44.0222 | 45.5111 | 47 | 48.9778 | 50.9556 | 52.9333 | 54.9111 | 56.8889 | 59.1111 | 61.3333 | 63.5556 | 65.7778 | 68 | 70.9778 | 73.9556 | 76.9333 | 79.9111 | 82.8889 | 86.2 | 89.5111 | 92.8222 | 96.1333 | 99.4444 | 103.5556 | 107.6667 | 111.7778 | 115.8889 | 120
4 | 1.6 | 4016 | 40.3333 | 41.9111 | 43.4889 | 45.0667 | 46.6444 | 48.2222 | 50.1556 | 52.0889 | 54.0222 | 55.9556 | 57.8889 | 60.3111 | 62.7333 | 65.1556 | 67.5778 | 70 | 72.8667 | 75.7333 | 78.6 | 81.4667 | 84.3333 | 87.9556 | 91.5778 | 95.2 | 98.8222 | 102.4444 | 106.4444 | 110.4444 | 114.4444 | 118.4444 | 122.4444
4 | 1.8 | 4018 | 41.5556 | 43.0889 | 44.6222 | 46.1556 | 47.6889 | 49.2222 | 51.2 | 53.1778 | 55.1556 | 57.1333 | 59.1111 | 61.5333 | 63.9556 | 66.3778 | 68.8 | 71.2222 | 74.2889 | 77.3556 | 80.4222 | 83.4889 | 86.5556 | 90.2222 | 93.8889 | 97.5556 | 101.2222 | 104.8889 | 109.0444 | 113.2 | 117.3556 | 121.5111 | 125.6667
4 | 2 | 4020 | 42.5556 | 44.1333 | 45.7111 | 47.2889 | 48.8667 | 50.4444 | 52.4222 | 54.4 | 56.3778 | 58.3556 | 60.3333 | 62.9111 | 65.4889 | 68.0667 | 70.6444 | 73.2222 | 76.2889 | 79.3556 | 82.4222 | 85.4889 | 88.5556 | 92.2667 | 95.9778 | 99.6889 | 103.4 | 107.1111 | 111.4667 | 115.8222 | 120.1778 | 124.5333 | 128.8889
4 | 2.2 | 4022 | 42.7778 | 44.5111 | 46.2444 | 47.9778 | 49.7111 | 51.4444 | 53.4667 | 55.4889 | 57.5111 | 59.5333 | 61.5556 | 64.2222 | 66.8889 | 69.5556 | 72.2222 | 74.8889 | 78.0667 | 81.2444 | 84.4222 | 87.6 | 90.7778 | 94.4889 | 98.2 | 101.9111 | 105.6222 | 109.3333 | 113.6889 | 118.0444 | 122.4 | 126.7556 | 131.1111
4 | 2.4 | 4024 | 43.7778 | 45.5111 | 47.2444 | 48.9778 | 50.7111 | 52.4444 | 54.4667 | 56.4889 | 58.5111 | 60.5333 | 62.5556 | 65.3333 | 68.1111 | 70.8889 | 73.6667 | 76.4444 | 79.5556 | 82.6667 | 85.7778 | 88.8889 | 92 | 95.9111 | 99.8222 | 103.7333 | 107.6444 | 111.5556 | 116.1111 | 120.6667 | 125.2222 | 129.7778 | 134.3333
4 | 2.6 | 4026 | 44.7778 | 46.5556 | 48.3333 | 50.1111 | 51.8889 | 53.6667 | 55.6889 | 57.7111 | 59.7333 | 61.7556 | 63.7778 | 66.5556 | 69.3333 | 72.1111 | 74.8889 | 77.6667 | 80.9778 | 84.2889 | 87.6 | 90.9111 | 94.2222 | 98.1333 | 102.0444 | 105.9556 | 109.8667 | 113.7778 | 118.3778 | 122.9778 | 127.5778 | 132.1778 | 136.7778
4 | 2.8 | 4028 | 45 | 46.7778 | 48.5556 | 50.3333 | 52.1111 | 53.8889 | 56.1111 | 58.3333 | 60.5556 | 62.7778 | 65 | 67.7778 | 70.5556 | 73.3333 | 76.1111 | 78.8889 | 82.3556 | 85.8222 | 89.2889 | 92.7556 | 96.2222 | 100.1778 | 104.1333 | 108.0889 | 112.0444 | 116 | 120.6 | 125.2 | 129.8 | 134.4 | 139
4 | 3 | 4030 | 46 | 47.7778 | 49.5556 | 51.3333 | 53.1111 | 54.8889 | 57.2667 | 59.6444 | 62.0222 | 64.4 | 66.7778 | 69.6 | 72.4222 | 75.2444 | 78.0667 | 80.8889 | 84.2 | 87.5111 | 90.8222 | 94.1333 | 97.4444 | 101.5556 | 105.6667 | 109.7778 | 113.8889 | 118 | 122.8 | 127.6 | 132.4 | 137.2 | 142
5 | 0 | 5000 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 81.8 | 84.6 | 87.4 | 90.2 | 93
5 | 0.2 | 5002 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 81.8 | 84.6 | 87.4 | 90.2 | 93
5 | 0.4 | 5004 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 81.8 | 84.6 | 87.4 | 90.2 | 93
5 | 0.6 | 5006 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.6 | 73.2 | 75.8 | 78.4 | 81 | 84.2 | 87.4 | 90.6 | 93.8 | 97
5 | 0.8 | 5008 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 50.8 | 52.6 | 54.4 | 56.2 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.2 | 90.4 | 93.6 | 96.8 | 100
5 | 1 | 5010 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 52 | 54 | 56 | 58 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 75 | 78 | 81 | 84 | 87 | 90.4 | 93.8 | 97.2 | 100.6 | 104
5 | 1.2 | 5012 | 36 | 37.2 | 38.4 | 39.6 | 40.8 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53 | 55 | 57 | 59 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.6 | 96.2 | 99.8 | 103.4 | 107
5 | 1.4 | 5014 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54 | 56 | 58 | 60 | 62 | 64.8 | 67.6 | 70.4 | 73.2 | 76 | 79 | 82 | 85 | 88 | 91 | 94.8 | 98.6 | 102.4 | 106.2 | 110
5 | 1.6 | 5016 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 80.4 | 83.8 | 87.2 | 90.6 | 94 | 97.6 | 101.2 | 104.8 | 108.4 | 112
5 | 1.8 | 5018 | 38 | 39.4 | 40.8 | 42.2 | 43.6 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 82.4 | 85.8 | 89.2 | 92.6 | 96 | 99.8 | 103.6 | 107.4 | 111.2 | 115
5 | 2 | 5020 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.4 | 87.8 | 91.2 | 94.6 | 98 | 102 | 106 | 110 | 114 | 118
5 | 2.2 | 5022 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56 | 58.4 | 60.8 | 63.2 | 65.6 | 68 | 71 | 74 | 77 | 80 | 83 | 86.4 | 89.8 | 93.2 | 96.6 | 100 | 104 | 108 | 112 | 116 | 120
5 | 2.4 | 5024 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.6 | 62.2 | 64.8 | 67.4 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.6 | 91.2 | 94.8 | 98.4 | 102 | 106.2 | 110.4 | 114.6 | 118.8 | 123
5 | 2.6 | 5026 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 50.8 | 52.6 | 54.4 | 56.2 | 58 | 60.6 | 63.2 | 65.8 | 68.4 | 71 | 74 | 77 | 80 | 83 | 86 | 89.6 | 93.2 | 96.8 | 100.4 | 104 | 108.2 | 112.4 | 116.6 | 120.8 | 125
5 | 2.8 | 5028 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51 | 53 | 55 | 57 | 59 | 61.6 | 64.2 | 66.8 | 69.4 | 72 | 75.2 | 78.4 | 81.6 | 84.8 | 88 | 91.6 | 95.2 | 98.8 | 102.4 | 106 | 110.2 | 114.4 | 118.6 | 122.8 | 127
5 | 3 | 5030 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 52.2 | 54.4 | 56.6 | 58.8 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.8 | 96.6 | 100.4 | 104.2 | 108 | 112.4 | 116.8 | 121.2 | 125.6 | 130
6 | 0 | 6000 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.52 | 47.24 | 48.96 | 50.68 | 52.4 | 54.48 | 56.56 | 58.64 | 60.72 | 62.8 | 65.24 | 67.68 | 70.12 | 72.56 | 75 | 77.68 | 80.36 | 83.04 | 85.72 | 88.4
6 | 0.2 | 6002 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.52 | 47.24 | 48.96 | 50.68 | 52.4 | 54.48 | 56.56 | 58.64 | 60.72 | 62.8 | 65.24 | 67.68 | 70.12 | 72.56 | 75 | 77.68 | 80.36 | 83.04 | 85.72 | 88.4
6 | 0.4 | 6004 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.52 | 47.24 | 48.96 | 50.68 | 52.4 | 54.48 | 56.56 | 58.64 | 60.72 | 62.8 | 65.24 | 67.68 | 70.12 | 72.56 | 75 | 77.68 | 80.36 | 83.04 | 85.72 | 88.4
6 | 0.6 | 6006 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.32 | 49.04 | 50.76 | 52.48 | 54.2 | 56.28 | 58.36 | 60.44 | 62.52 | 64.6 | 67.08 | 69.56 | 72.04 | 74.52 | 77 | 80.04 | 83.08 | 86.12 | 89.16 | 92.2
6 | 0.8 | 6008 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.32 | 50.04 | 51.76 | 53.48 | 55.2 | 57.48 | 59.76 | 62.04 | 64.32 | 66.6 | 69.24 | 71.88 | 74.52 | 77.16 | 79.8 | 82.84 | 85.88 | 88.92 | 91.96 | 95
6 | 1 | 6010 | 33.2 | 34.52 | 35.84 | 37.16 | 38.48 | 39.8 | 41.32 | 42.84 | 44.36 | 45.88 | 47.4 | 49.32 | 51.24 | 53.16 | 55.08 | 57 | 59.28 | 61.56 | 63.84 | 66.12 | 68.4 | 71.24 | 74.08 | 76.92 | 79.76 | 82.6 | 85.84 | 89.08 | 92.32 | 95.56 | 98.8
6 | 1.2 | 6012 | 34.2 | 35.36 | 36.52 | 37.68 | 38.84 | 40 | 41.68 | 43.36 | 45.04 | 46.72 | 48.4 | 50.32 | 52.24 | 54.16 | 56.08 | 58 | 60.44 | 62.88 | 65.32 | 67.76 | 70.2 | 73.08 | 75.96 | 78.84 | 81.72 | 84.6 | 88 | 91.4 | 94.8 | 98.2 | 101.6
6 | 1.4 | 6014 | 34.2 | 35.56 | 36.92 | 38.28 | 39.64 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4 | 51.32 | 53.24 | 55.16 | 57.08 | 59 | 61.64 | 64.28 | 66.92 | 69.56 | 72.2 | 75.08 | 77.96 | 80.84 | 83.72 | 86.6 | 90.16 | 93.72 | 97.28 | 100.84 | 104.4
6 | 1.6 | 6016 | 35.2 | 36.52 | 37.84 | 39.16 | 40.48 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8 | 63.28 | 65.76 | 68.24 | 70.72 | 73.2 | 76.4 | 79.6 | 82.8 | 86 | 89.2 | 92.64 | 96.08 | 99.52 | 102.96 | 106.4
6 | 1.8 | 6018 | 36.2 | 37.52 | 38.84 | 40.16 | 41.48 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.48 | 55.56 | 57.64 | 59.72 | 61.8 | 64.48 | 67.16 | 69.84 | 72.52 | 75.2 | 78.4 | 81.6 | 84.8 | 88 | 91.2 | 94.8 | 98.4 | 102 | 105.6 | 109.2
6 | 2 | 6020 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.48 | 47.16 | 48.84 | 50.52 | 52.2 | 54.48 | 56.76 | 59.04 | 61.32 | 63.6 | 66.28 | 68.96 | 71.64 | 74.32 | 77 | 80.24 | 83.48 | 86.72 | 89.96 | 93.2 | 96.96 | 100.72 | 104.48 | 108.24 | 112
6 | 2.2 | 6022 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.48 | 57.76 | 60.04 | 62.32 | 64.6 | 67.44 | 70.28 | 73.12 | 75.96 | 78.8 | 82.04 | 85.28 | 88.52 | 91.76 | 95 | 98.8 | 102.6 | 106.4 | 110.2 | 114
6 | 2.4 | 6024 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.32 | 49.04 | 50.76 | 52.48 | 54.2 | 56.64 | 59.08 | 61.52 | 63.96 | 66.4 | 69.08 | 71.76 | 74.44 | 77.12 | 79.8 | 83.24 | 86.68 | 90.12 | 93.56 | 97 | 100.96 | 104.92 | 108.88 | 112.84 | 116.8
6 | 2.6 | 6026 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.32 | 50.04 | 51.76 | 53.48 | 55.2 | 57.64 | 60.08 | 62.52 | 64.96 | 67.4 | 70.28 | 73.16 | 76.04 | 78.92 | 81.8 | 85.2 | 88.6 | 92 | 95.4 | 98.8 | 102.8 | 106.8 | 110.8 | 114.8 | 118.8
6 | 2.8 | 6028 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.52 | 50.44 | 52.36 | 54.28 | 56.2 | 58.64 | 61.08 | 63.52 | 65.96 | 68.4 | 71.44 | 74.48 | 77.52 | 80.56 | 83.6 | 87.04 | 90.48 | 93.92 | 97.36 | 100.8 | 104.8 | 108.8 | 112.8 | 116.8 | 120.8
6 | 3 | 6030 | 40 | 41.52 | 43.04 | 44.56 | 46.08 | 47.6 | 49.68 | 51.76 | 53.84 | 55.92 | 58 | 60.44 | 62.88 | 65.32 | 67.76 | 70.2 | 73.08 | 75.96 | 78.84 | 81.72 | 84.6 | 88.2 | 91.8 | 95.4 | 99 | 102.6 | 106.76 | 110.92 | 115.08 | 119.24 | 123.4
7 | 0 | 7000 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.24 | 44.88 | 46.52 | 48.16 | 49.8 | 51.76 | 53.72 | 55.68 | 57.64 | 59.6 | 61.88 | 64.16 | 66.44 | 68.72 | 71 | 73.56 | 76.12 | 78.68 | 81.24 | 83.8
7 | 0.2 | 7002 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.24 | 44.88 | 46.52 | 48.16 | 49.8 | 51.76 | 53.72 | 55.68 | 57.64 | 59.6 | 61.88 | 64.16 | 66.44 | 68.72 | 71 | 73.56 | 76.12 | 78.68 | 81.24 | 83.8
7 | 0.4 | 7004 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.24 | 44.88 | 46.52 | 48.16 | 49.8 | 51.76 | 53.72 | 55.68 | 57.64 | 59.6 | 61.88 | 64.16 | 66.44 | 68.72 | 71 | 73.56 | 76.12 | 78.68 | 81.24 | 83.8
7 | 0.6 | 7006 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.84 | 46.48 | 48.12 | 49.76 | 51.4 | 53.36 | 55.32 | 57.28 | 59.24 | 61.2 | 63.56 | 65.92 | 68.28 | 70.64 | 73 | 75.88 | 78.76 | 81.64 | 84.52 | 87.4
7 | 0.8 | 7008 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.84 | 47.48 | 49.12 | 50.76 | 52.4 | 54.56 | 56.72 | 58.88 | 61.04 | 63.2 | 65.68 | 68.16 | 70.64 | 73.12 | 75.6 | 78.48 | 81.36 | 84.24 | 87.12 | 90
7 | 1 | 7010 | 31.4 | 32.64 | 33.88 | 35.12 | 36.36 | 37.6 | 39.04 | 40.48 | 41.92 | 43.36 | 44.8 | 46.64 | 48.48 | 50.32 | 52.16 | 54 | 56.16 | 58.32 | 60.48 | 62.64 | 64.8 | 67.48 | 70.16 | 72.84 | 75.52 | 78.2 | 81.28 | 84.36 | 87.44 | 90.52 | 93.6
7 | 1.2 | 7012 | 32.4 | 33.52 | 34.64 | 35.76 | 36.88 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.64 | 49.48 | 51.32 | 53.16 | 55 | 57.28 | 59.56 | 61.84 | 64.12 | 66.4 | 69.16 | 71.92 | 74.68 | 77.44 | 80.2 | 83.4 | 86.6 | 89.8 | 93 | 96.2
7 | 1.4 | 7014 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.64 | 50.48 | 52.32 | 54.16 | 56 | 58.48 | 60.96 | 63.44 | 65.92 | 68.4 | 71.16 | 73.92 | 76.68 | 79.44 | 82.2 | 85.52 | 88.84 | 92.16 | 95.48 | 98.8
7 | 1.6 | 7016 | 33.4 | 34.64 | 35.88 | 37.12 | 38.36 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6 | 59.96 | 62.32 | 64.68 | 67.04 | 69.4 | 72.4 | 75.4 | 78.4 | 81.4 | 84.4 | 87.68 | 90.96 | 94.24 | 97.52 | 100.8
7 | 1.8 | 7018 | 34.4 | 35.64 | 36.88 | 38.12 | 39.36 | 40.6 | 42.24 | 43.88 | 45.52 | 47.16 | 48.8 | 50.76 | 52.72 | 54.68 | 56.64 | 58.6 | 61.16 | 63.72 | 66.28 | 68.84 | 71.4 | 74.4 | 77.4 | 80.4 | 83.4 | 86.4 | 89.8 | 93.2 | 96.6 | 100 | 103.4
7 | 2 | 7020 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.16 | 44.72 | 46.28 | 47.84 | 49.4 | 51.56 | 53.72 | 55.88 | 58.04 | 60.2 | 62.76 | 65.32 | 67.88 | 70.44 | 73 | 76.08 | 79.16 | 82.24 | 85.32 | 88.4 | 91.92 | 95.44 | 98.96 | 102.48 | 106
7 | 2.2 | 7022 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4 | 52.56 | 54.72 | 56.88 | 59.04 | 61.2 | 63.88 | 66.56 | 69.24 | 71.92 | 74.6 | 77.68 | 80.76 | 83.84 | 86.92 | 90 | 93.6 | 97.2 | 100.8 | 104.4 | 108
7 | 2.4 | 7024 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.84 | 46.48 | 48.12 | 49.76 | 51.4 | 53.68 | 55.96 | 58.24 | 60.52 | 62.8 | 65.36 | 67.92 | 70.48 | 73.04 | 75.6 | 78.88 | 82.16 | 85.44 | 88.72 | 92 | 95.72 | 99.44 | 103.16 | 106.88 | 110.6
7 | 2.6 | 7026 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.84 | 47.48 | 49.12 | 50.76 | 52.4 | 54.68 | 56.96 | 59.24 | 61.52 | 63.8 | 66.56 | 69.32 | 72.08 | 74.84 | 77.6 | 80.8 | 84 | 87.2 | 90.4 | 93.6 | 97.4 | 101.2 | 105 | 108.8 | 112.6
7 | 2.8 | 7028 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 46.04 | 47.88 | 49.72 | 51.56 | 53.4 | 55.68 | 57.96 | 60.24 | 62.52 | 64.8 | 67.68 | 70.56 | 73.44 | 76.32 | 79.2 | 82.48 | 85.76 | 89.04 | 92.32 | 95.6 | 99.4 | 103.2 | 107 | 110.8 | 114.6
7 | 3 | 7030 | 38 | 39.44 | 40.88 | 42.32 | 43.76 | 45.2 | 47.16 | 49.12 | 51.08 | 53.04 | 55 | 57.28 | 59.56 | 61.84 | 64.12 | 66.4 | 69.16 | 71.92 | 74.68 | 77.44 | 80.2 | 83.6 | 87 | 90.4 | 93.8 | 97.2 | 101.12 | 105.04 | 108.96 | 112.88 | 116.8
8 | 0 | 8000 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.96 | 42.52 | 44.08 | 45.64 | 47.2 | 49.04 | 50.88 | 52.72 | 54.56 | 56.4 | 58.52 | 60.64 | 62.76 | 64.88 | 67 | 69.44 | 71.88 | 74.32 | 76.76 | 79.2
8 | 0.2 | 8002 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.96 | 42.52 | 44.08 | 45.64 | 47.2 | 49.04 | 50.88 | 52.72 | 54.56 | 56.4 | 58.52 | 60.64 | 62.76 | 64.88 | 67 | 69.44 | 71.88 | 74.32 | 76.76 | 79.2
8 | 0.4 | 8004 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.96 | 42.52 | 44.08 | 45.64 | 47.2 | 49.04 | 50.88 | 52.72 | 54.56 | 56.4 | 58.52 | 60.64 | 62.76 | 64.88 | 67 | 69.44 | 71.88 | 74.32 | 76.76 | 79.2
8 | 0.6 | 8006 | 28.2 | 29.36 | 30.52 | 31.68 | 32.84 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.36 | 43.92 | 45.48 | 47.04 | 48.6 | 50.44 | 52.28 | 54.12 | 55.96 | 57.8 | 60.04 | 62.28 | 64.52 | 66.76 | 69 | 71.72 | 74.44 | 77.16 | 79.88 | 82.6
8 | 0.8 | 8008 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.36 | 44.92 | 46.48 | 48.04 | 49.6 | 51.64 | 53.68 | 55.72 | 57.76 | 59.8 | 62.12 | 64.44 | 66.76 | 69.08 | 71.4 | 74.12 | 76.84 | 79.56 | 82.28 | 85
8 | 1 | 8010 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2 | 43.96 | 45.72 | 47.48 | 49.24 | 51 | 53.04 | 55.08 | 57.12 | 59.16 | 61.2 | 63.72 | 66.24 | 68.76 | 71.28 | 73.8 | 76.72 | 79.64 | 82.56 | 85.48 | 88.4
8 | 1.2 | 8012 | 30.6 | 31.68 | 32.76 | 33.84 | 34.92 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52 | 54.12 | 56.24 | 58.36 | 60.48 | 62.6 | 65.24 | 67.88 | 70.52 | 73.16 | 75.8 | 78.8 | 81.8 | 84.8 | 87.8 | 90.8
8 | 1.4 | 8014 | 30.6 | 31.88 | 33.16 | 34.44 | 35.72 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53 | 55.32 | 57.64 | 59.96 | 62.28 | 64.6 | 67.24 | 69.88 | 72.52 | 75.16 | 77.8 | 80.88 | 83.96 | 87.04 | 90.12 | 93.2
8 | 1.6 | 8016 | 31.6 | 32.76 | 33.92 | 35.08 | 36.24 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.04 | 48.88 | 50.72 | 52.56 | 54.4 | 56.64 | 58.88 | 61.12 | 63.36 | 65.6 | 68.4 | 71.2 | 74 | 76.8 | 79.6 | 82.72 | 85.84 | 88.96 | 92.08 | 95.2
8 | 1.8 | 8018 | 32.6 | 33.76 | 34.92 | 36.08 | 37.24 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.04 | 49.88 | 51.72 | 53.56 | 55.4 | 57.84 | 60.28 | 62.72 | 65.16 | 67.6 | 70.4 | 73.2 | 76 | 78.8 | 81.6 | 84.8 | 88 | 91.2 | 94.4 | 97.6
8 | 2 | 8020 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.84 | 42.28 | 43.72 | 45.16 | 46.6 | 48.64 | 50.68 | 52.72 | 54.76 | 56.8 | 59.24 | 61.68 | 64.12 | 66.56 | 69 | 71.92 | 74.84 | 77.76 | 80.68 | 83.6 | 86.88 | 90.16 | 93.44 | 96.72 | 100
8 | 2.2 | 8022 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.36 | 42.92 | 44.48 | 46.04 | 47.6 | 49.64 | 51.68 | 53.72 | 55.76 | 57.8 | 60.32 | 62.84 | 65.36 | 67.88 | 70.4 | 73.32 | 76.24 | 79.16 | 82.08 | 85 | 88.4 | 91.8 | 95.2 | 98.6 | 102
8 | 2.4 | 8024 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.36 | 43.92 | 45.48 | 47.04 | 48.6 | 50.72 | 52.84 | 54.96 | 57.08 | 59.2 | 61.64 | 64.08 | 66.52 | 68.96 | 71.4 | 74.52 | 77.64 | 80.76 | 83.88 | 87 | 90.48 | 93.96 | 97.44 | 100.92 | 104.4
8 | 2.6 | 8026 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.36 | 44.92 | 46.48 | 48.04 | 49.6 | 51.72 | 53.84 | 55.96 | 58.08 | 60.2 | 62.84 | 65.48 | 68.12 | 70.76 | 73.4 | 76.4 | 79.4 | 82.4 | 85.4 | 88.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4
8 | 2.8 | 8028 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.56 | 45.32 | 47.08 | 48.84 | 50.6 | 52.72 | 54.84 | 56.96 | 59.08 | 61.2 | 63.92 | 66.64 | 69.36 | 72.08 | 74.8 | 77.92 | 81.04 | 84.16 | 87.28 | 90.4 | 94 | 97.6 | 101.2 | 104.8 | 108.4
8 | 3 | 8030 | 36 | 37.36 | 38.72 | 40.08 | 41.44 | 42.8 | 44.64 | 46.48 | 48.32 | 50.16 | 52 | 54.12 | 56.24 | 58.36 | 60.48 | 62.6 | 65.24 | 67.88 | 70.52 | 73.16 | 75.8 | 79 | 82.2 | 85.4 | 88.6 | 91.8 | 95.48 | 99.16 | 102.84 | 106.52 | 110.2
9 | 0 | 9000 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.16 | 57.12 | 59.08 | 61.04 | 63 | 65.32 | 67.64 | 69.96 | 72.28 | 74.6
9 | 0.2 | 9002 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.16 | 57.12 | 59.08 | 61.04 | 63 | 65.32 | 67.64 | 69.96 | 72.28 | 74.6
9 | 0.4 | 9004 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.16 | 57.12 | 59.08 | 61.04 | 63 | 65.32 | 67.64 | 69.96 | 72.28 | 74.6
9 | 0.6 | 9006 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.88 | 41.36 | 42.84 | 44.32 | 45.8 | 47.52 | 49.24 | 50.96 | 52.68 | 54.4 | 56.52 | 58.64 | 60.76 | 62.88 | 65 | 67.56 | 70.12 | 72.68 | 75.24 | 77.8
9 | 0.8 | 9008 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.88 | 42.36 | 43.84 | 45.32 | 46.8 | 48.72 | 50.64 | 52.56 | 54.48 | 56.4 | 58.56 | 60.72 | 62.88 | 65.04 | 67.2 | 69.76 | 72.32 | 74.88 | 77.44 | 80
9 | 1 | 9010 | 27.8 | 28.88 | 29.96 | 31.04 | 32.12 | 33.2 | 34.48 | 35.76 | 37.04 | 38.32 | 39.6 | 41.28 | 42.96 | 44.64 | 46.32 | 48 | 49.92 | 51.84 | 53.76 | 55.68 | 57.6 | 59.96 | 62.32 | 64.68 | 67.04 | 69.4 | 72.16 | 74.92 | 77.68 | 80.44 | 83.2
9 | 1.2 | 9012 | 28.8 | 29.84 | 30.88 | 31.92 | 32.96 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.28 | 43.96 | 45.64 | 47.32 | 49 | 50.96 | 52.92 | 54.88 | 56.84 | 58.8 | 61.32 | 63.84 | 66.36 | 68.88 | 71.4 | 74.2 | 77 | 79.8 | 82.6 | 85.4
9 | 1.4 | 9014 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.28 | 44.96 | 46.64 | 48.32 | 50 | 52.16 | 54.32 | 56.48 | 58.64 | 60.8 | 63.32 | 65.84 | 68.36 | 70.88 | 73.4 | 76.24 | 79.08 | 81.92 | 84.76 | 87.6
9 | 1.6 | 9016 | 29.8 | 30.88 | 31.96 | 33.04 | 34.12 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.32 | 46.04 | 47.76 | 49.48 | 51.2 | 53.32 | 55.44 | 57.56 | 59.68 | 61.8 | 64.4 | 67 | 69.6 | 72.2 | 74.8 | 77.76 | 80.72 | 83.68 | 86.64 | 89.6
9 | 1.8 | 9018 | 30.8 | 31.88 | 32.96 | 34.04 | 35.12 | 36.2 | 37.68 | 39.16 | 40.64 | 42.12 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2 | 54.52 | 56.84 | 59.16 | 61.48 | 63.8 | 66.4 | 69 | 71.6 | 74.2 | 76.8 | 79.8 | 82.8 | 85.8 | 88.8 | 91.8
9 | 2 | 9020 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.52 | 39.84 | 41.16 | 42.48 | 43.8 | 45.72 | 47.64 | 49.56 | 51.48 | 53.4 | 55.72 | 58.04 | 60.36 | 62.68 | 65 | 67.76 | 70.52 | 73.28 | 76.04 | 78.8 | 81.84 | 84.88 | 87.92 | 90.96 | 94
9 | 2.2 | 9022 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8 | 46.72 | 48.64 | 50.56 | 52.48 | 54.4 | 56.76 | 59.12 | 61.48 | 63.84 | 66.2 | 68.96 | 71.72 | 74.48 | 77.24 | 80 | 83.2 | 86.4 | 89.6 | 92.8 | 96
9 | 2.4 | 9024 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.88 | 41.36 | 42.84 | 44.32 | 45.8 | 47.76 | 49.72 | 51.68 | 53.64 | 55.6 | 57.92 | 60.24 | 62.56 | 64.88 | 67.2 | 70.16 | 73.12 | 76.08 | 79.04 | 82 | 85.24 | 88.48 | 91.72 | 94.96 | 98.2
9 | 2.6 | 9026 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.88 | 42.36 | 43.84 | 45.32 | 46.8 | 48.76 | 50.72 | 52.68 | 54.64 | 56.6 | 59.12 | 61.64 | 64.16 | 66.68 | 69.2 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86.6 | 90 | 93.4 | 96.8 | 100.2
9 | 2.8 | 9028 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 41.08 | 42.76 | 44.44 | 46.12 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6 | 60.16 | 62.72 | 65.28 | 67.84 | 70.4 | 73.36 | 76.32 | 79.28 | 82.24 | 85.2 | 88.6 | 92 | 95.4 | 98.8 | 102.2
9 | 3 | 9030 | 34 | 35.28 | 36.56 | 37.84 | 39.12 | 40.4 | 42.12 | 43.84 | 45.56 | 47.28 | 49 | 50.96 | 52.92 | 54.88 | 56.84 | 58.8 | 61.32 | 63.84 | 66.36 | 68.88 | 71.4 | 74.4 | 77.4 | 80.4 | 83.4 | 86.4 | 89.84 | 93.28 | 96.72 | 100.16 | 103.6
10 | 0 | 10000 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70
10 | 0.2 | 10002 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70
10 | 0.4 | 10004 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70
10 | 0.6 | 10006 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.6 | 46.2 | 47.8 | 49.4 | 51 | 53 | 55 | 57 | 59 | 61 | 63.4 | 65.8 | 68.2 | 70.6 | 73
10 | 0.8 | 10008 | 26 | 27 | 28 | 29 | 30 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55 | 57 | 59 | 61 | 63 | 65.4 | 67.8 | 70.2 | 72.6 | 75
10 | 1 | 10010 | 26 | 27 | 28 | 29 | 30 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78
10 | 1.2 | 10012 | 27 | 28 | 29 | 30 | 31 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.6 | 72.2 | 74.8 | 77.4 | 80
10 | 1.4 | 10014 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 49 | 51 | 53 | 55 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.6 | 74.2 | 76.8 | 79.4 | 82
10 | 1.6 | 10016 | 28 | 29 | 30 | 31 | 32 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 50 | 52 | 54 | 56 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84
10 | 1.8 | 10018 | 29 | 30 | 31 | 32 | 33 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51.2 | 53.4 | 55.6 | 57.8 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86
10 | 2 | 10020 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.2 | 37.4 | 38.6 | 39.8 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 52.2 | 54.4 | 56.6 | 58.8 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 76.8 | 79.6 | 82.4 | 85.2 | 88
10 | 2.2 | 10022 | 30 | 31 | 32 | 33 | 34 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53.2 | 55.4 | 57.6 | 59.8 | 62 | 64.6 | 67.2 | 69.8 | 72.4 | 75 | 78 | 81 | 84 | 87 | 90
10 | 2.4 | 10024 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63 | 65.8 | 68.6 | 71.4 | 74.2 | 77 | 80 | 83 | 86 | 89 | 92
10 | 2.6 | 10026 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.4 | 57.8 | 60.2 | 62.6 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78 | 81.2 | 84.4 | 87.6 | 90.8 | 94
10 | 2.8 | 10028 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.4 | 58.8 | 61.2 | 63.6 | 66 | 68.8 | 71.6 | 74.4 | 77.2 | 80 | 83.2 | 86.4 | 89.6 | 92.8 | 96
10 | 3 | 10030 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.2 | 87.4 | 90.6 | 93.8 | 97
11 | 0 | 11000 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.28 | 29.36 | 30.44 | 31.52 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.68 | 42.16 | 43.64 | 45.12 | 46.6 | 48.28 | 49.96 | 51.64 | 53.32 | 55 | 57.08 | 59.16 | 61.24 | 63.32 | 65.4
11 | 0.2 | 11002 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.28 | 29.36 | 30.44 | 31.52 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.68 | 42.16 | 43.64 | 45.12 | 46.6 | 48.28 | 49.96 | 51.64 | 53.32 | 55 | 57.08 | 59.16 | 61.24 | 63.32 | 65.4
11 | 0.4 | 11004 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.28 | 29.36 | 30.44 | 31.52 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.68 | 42.16 | 43.64 | 45.12 | 46.6 | 48.28 | 49.96 | 51.64 | 53.32 | 55 | 57.08 | 59.16 | 61.24 | 63.32 | 65.4
11 | 0.6 | 11006 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2 | 41.68 | 43.16 | 44.64 | 46.12 | 47.6 | 49.48 | 51.36 | 53.24 | 55.12 | 57 | 59.24 | 61.48 | 63.72 | 65.96 | 68.2
11 | 0.8 | 11008 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 29.92 | 31.04 | 32.16 | 33.28 | 34.4 | 35.72 | 37.04 | 38.36 | 39.68 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4 | 51.28 | 53.16 | 55.04 | 56.92 | 58.8 | 61.04 | 63.28 | 65.52 | 67.76 | 70
11 | 1 | 11010 | 24.4 | 25.32 | 26.24 | 27.16 | 28.08 | 29 | 30.12 | 31.24 | 32.36 | 33.48 | 34.6 | 36.08 | 37.56 | 39.04 | 40.52 | 42 | 43.68 | 45.36 | 47.04 | 48.72 | 50.4 | 52.44 | 54.48 | 56.52 | 58.56 | 60.6 | 63.04 | 65.48 | 67.92 | 70.36 | 72.8
11 | 1.2 | 11012 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.92 | 38.44 | 39.96 | 41.48 | 43 | 44.68 | 46.36 | 48.04 | 49.72 | 51.4 | 53.64 | 55.88 | 58.12 | 60.36 | 62.6 | 65 | 67.4 | 69.8 | 72.2 | 74.6
11 | 1.4 | 11014 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8 | 45.68 | 47.56 | 49.44 | 51.32 | 53.2 | 55.44 | 57.68 | 59.92 | 62.16 | 64.4 | 66.84 | 69.28 | 71.72 | 74.16 | 76.6
11 | 1.6 | 11016 | 26.2 | 27.12 | 28.04 | 28.96 | 29.88 | 30.8 | 32.08 | 33.36 | 34.64 | 35.92 | 37.2 | 38.72 | 40.24 | 41.76 | 43.28 | 44.8 | 46.68 | 48.56 | 50.44 | 52.32 | 54.2 | 56.44 | 58.68 | 60.92 | 63.16 | 65.4 | 68 | 70.6 | 73.2 | 75.8 | 78.4
11 | 1.8 | 11018 | 27 | 27.96 | 28.92 | 29.88 | 30.84 | 31.8 | 33.08 | 34.36 | 35.64 | 36.92 | 38.2 | 39.72 | 41.24 | 42.76 | 44.28 | 45.8 | 47.84 | 49.88 | 51.92 | 53.96 | 56 | 58.24 | 60.48 | 62.72 | 64.96 | 67.2 | 69.84 | 72.48 | 75.12 | 77.76 | 80.4
11 | 2 | 11020 | 27 | 28.12 | 29.24 | 30.36 | 31.48 | 32.6 | 33.76 | 34.92 | 36.08 | 37.24 | 38.4 | 40.04 | 41.68 | 43.32 | 44.96 | 46.6 | 48.68 | 50.76 | 52.84 | 54.92 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.64 | 74.28 | 76.92 | 79.56 | 82.2
11 | 2.2 | 11022 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.88 | 42.56 | 44.24 | 45.92 | 47.6 | 49.64 | 51.68 | 53.72 | 55.76 | 57.8 | 60.24 | 62.68 | 65.12 | 67.56 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84
11 | 2.4 | 11024 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2 | 41.88 | 43.56 | 45.24 | 46.92 | 48.6 | 50.64 | 52.68 | 54.72 | 56.76 | 58.8 | 61.4 | 64 | 66.6 | 69.2 | 71.8 | 74.6 | 77.4 | 80.2 | 83 | 85.8
11 | 2.6 | 11026 | 28.8 | 29.92 | 31.04 | 32.16 | 33.28 | 34.4 | 35.72 | 37.04 | 38.36 | 39.68 | 41 | 42.72 | 44.44 | 46.16 | 47.88 | 49.6 | 51.8 | 54 | 56.2 | 58.4 | 60.6 | 63.04 | 65.48 | 67.92 | 70.36 | 72.8 | 75.8 | 78.8 | 81.8 | 84.8 | 87.8
11 | 2.8 | 11028 | 29 | 30.12 | 31.24 | 32.36 | 33.48 | 34.6 | 36.08 | 37.56 | 39.04 | 40.52 | 42 | 43.68 | 45.36 | 47.04 | 48.72 | 50.4 | 52.64 | 54.88 | 57.12 | 59.36 | 61.6 | 64.2 | 66.8 | 69.4 | 72 | 74.6 | 77.6 | 80.6 | 83.6 | 86.6 | 89.6
11 | 3 | 11030 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.88 | 38.36 | 39.84 | 41.32 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.64 | 55.88 | 58.12 | 60.36 | 62.6 | 65.2 | 67.8 | 70.4 | 73 | 75.6 | 78.6 | 81.6 | 84.6 | 87.6 | 90.6
12 | 0 | 12000 | 20.8 | 21.72 | 22.64 | 23.56 | 24.48 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.76 | 39.12 | 40.48 | 41.84 | 43.2 | 44.76 | 46.32 | 47.88 | 49.44 | 51 | 52.96 | 54.92 | 56.88 | 58.84 | 60.8
12 | 0.2 | 12002 | 20.8 | 21.72 | 22.64 | 23.56 | 24.48 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.76 | 39.12 | 40.48 | 41.84 | 43.2 | 44.76 | 46.32 | 47.88 | 49.44 | 51 | 52.96 | 54.92 | 56.88 | 58.84 | 60.8
12 | 0.4 | 12004 | 20.8 | 21.72 | 22.64 | 23.56 | 24.48 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.76 | 39.12 | 40.48 | 41.84 | 43.2 | 44.76 | 46.32 | 47.88 | 49.44 | 51 | 52.96 | 54.92 | 56.88 | 58.84 | 60.8
12 | 0.6 | 12006 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 38.76 | 40.12 | 41.48 | 42.84 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53 | 55.08 | 57.16 | 59.24 | 61.32 | 63.4
12 | 0.8 | 12008 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 33.04 | 34.28 | 35.52 | 36.76 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.56 | 49.32 | 51.08 | 52.84 | 54.6 | 56.68 | 58.76 | 60.84 | 62.92 | 65
12 | 1 | 12010 | 22.8 | 23.64 | 24.48 | 25.32 | 26.16 | 27 | 28.04 | 29.08 | 30.12 | 31.16 | 32.2 | 33.56 | 34.92 | 36.28 | 37.64 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.68 | 50.56 | 52.44 | 54.32 | 56.2 | 58.48 | 60.76 | 63.04 | 65.32 | 67.6
12 | 1.2 | 12012 | 23.4 | 24.24 | 25.08 | 25.92 | 26.76 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8 | 34.24 | 35.68 | 37.12 | 38.56 | 40 | 41.56 | 43.12 | 44.68 | 46.24 | 47.8 | 49.88 | 51.96 | 54.04 | 56.12 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.2
12 | 1.4 | 12014 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.64 | 30.68 | 31.72 | 32.76 | 33.8 | 35.16 | 36.52 | 37.88 | 39.24 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.48 | 53.56 | 55.64 | 57.72 | 59.8 | 62.08 | 64.36 | 66.64 | 68.92 | 71.2
12 | 1.6 | 12016 | 24.4 | 25.24 | 26.08 | 26.92 | 27.76 | 28.6 | 29.76 | 30.92 | 32.08 | 33.24 | 34.4 | 35.84 | 37.28 | 38.72 | 40.16 | 41.6 | 43.36 | 45.12 | 46.88 | 48.64 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8 | 63.2 | 65.6 | 68 | 70.4 | 72.8
12 | 1.8 | 12018 | 25 | 25.92 | 26.84 | 27.76 | 28.68 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4 | 36.84 | 38.28 | 39.72 | 41.16 | 42.6 | 44.48 | 46.36 | 48.24 | 50.12 | 52 | 54.08 | 56.16 | 58.24 | 60.32 | 62.4 | 64.88 | 67.36 | 69.84 | 72.32 | 74.8
12 | 2 | 12020 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.32 | 32.44 | 33.56 | 34.68 | 35.8 | 37.28 | 38.76 | 40.24 | 41.72 | 43.2 | 45.16 | 47.12 | 49.08 | 51.04 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64 | 66.48 | 68.96 | 71.44 | 73.92 | 76.4
12 | 2.2 | 12022 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.08 | 47.96 | 49.84 | 51.72 | 53.6 | 55.88 | 58.16 | 60.44 | 62.72 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78
12 | 2.4 | 12024 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.08 | 48.96 | 50.84 | 52.72 | 54.6 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 79.6
12 | 2.6 | 12026 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 33.04 | 34.28 | 35.52 | 36.76 | 38 | 39.64 | 41.28 | 42.92 | 44.56 | 46.2 | 48.2 | 50.2 | 52.2 | 54.2 | 56.2 | 58.48 | 60.76 | 63.04 | 65.32 | 67.6 | 70.4 | 73.2 | 76 | 78.8 | 81.6
12 | 2.8 | 12028 | 27 | 28.04 | 29.08 | 30.12 | 31.16 | 32.2 | 33.56 | 34.92 | 36.28 | 37.64 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.88 | 50.96 | 53.04 | 55.12 | 57.2 | 59.6 | 62 | 64.4 | 66.8 | 69.2 | 72 | 74.8 | 77.6 | 80.4 | 83.2
12 | 3 | 12030 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8 | 34.16 | 35.52 | 36.88 | 38.24 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.88 | 51.96 | 54.04 | 56.12 | 58.2 | 60.6 | 63 | 65.4 | 67.8 | 70.2 | 73 | 75.8 | 78.6 | 81.4 | 84.2
13 | 0 | 13000 | 19.2 | 20.08 | 20.96 | 21.84 | 22.72 | 23.6 | 24.44 | 25.28 | 26.12 | 26.96 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.24 | 42.68 | 44.12 | 45.56 | 47 | 48.84 | 50.68 | 52.52 | 54.36 | 56.2
13 | 0.2 | 13002 | 19.2 | 20.08 | 20.96 | 21.84 | 22.72 | 23.6 | 24.44 | 25.28 | 26.12 | 26.96 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.24 | 42.68 | 44.12 | 45.56 | 47 | 48.84 | 50.68 | 52.52 | 54.36 | 56.2
13 | 0.4 | 13004 | 19.2 | 20.08 | 20.96 | 21.84 | 22.72 | 23.6 | 24.44 | 25.28 | 26.12 | 26.96 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.24 | 42.68 | 44.12 | 45.56 | 47 | 48.84 | 50.68 | 52.52 | 54.36 | 56.2
13 | 0.6 | 13006 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6 | 35.84 | 37.08 | 38.32 | 39.56 | 40.8 | 42.44 | 44.08 | 45.72 | 47.36 | 49 | 50.92 | 52.84 | 54.76 | 56.68 | 58.6
13 | 0.8 | 13008 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.36 | 26.32 | 27.28 | 28.24 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.44 | 37.88 | 39.32 | 40.76 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4 | 52.32 | 54.24 | 56.16 | 58.08 | 60
13 | 1 | 13010 | 21.2 | 21.96 | 22.72 | 23.48 | 24.24 | 25 | 25.96 | 26.92 | 27.88 | 28.84 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.92 | 46.64 | 48.36 | 50.08 | 51.8 | 53.92 | 56.04 | 58.16 | 60.28 | 62.4
13 | 1.2 | 13012 | 21.6 | 22.36 | 23.12 | 23.88 | 24.64 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.56 | 32.92 | 34.28 | 35.64 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 46.12 | 48.04 | 49.96 | 51.88 | 53.8 | 55.8 | 57.8 | 59.8 | 61.8 | 63.8
13 | 1.4 | 13014 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.36 | 28.32 | 29.28 | 30.24 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 39.04 | 40.68 | 42.32 | 43.96 | 45.6 | 47.52 | 49.44 | 51.36 | 53.28 | 55.2 | 57.32 | 59.44 | 61.56 | 63.68 | 65.8
13 | 1.6 | 13016 | 22.6 | 23.36 | 24.12 | 24.88 | 25.64 | 26.4 | 27.44 | 28.48 | 29.52 | 30.56 | 31.6 | 32.96 | 34.32 | 35.68 | 37.04 | 38.4 | 40.04 | 41.68 | 43.32 | 44.96 | 46.6 | 48.52 | 50.44 | 52.36 | 54.28 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.2
13 | 1.8 | 13018 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.44 | 29.48 | 30.52 | 31.56 | 32.6 | 33.96 | 35.32 | 36.68 | 38.04 | 39.4 | 41.12 | 42.84 | 44.56 | 46.28 | 48 | 49.92 | 51.84 | 53.76 | 55.68 | 57.6 | 59.92 | 62.24 | 64.56 | 66.88 | 69.2
13 | 2 | 13020 | 23 | 23.96 | 24.92 | 25.88 | 26.84 | 27.8 | 28.88 | 29.96 | 31.04 | 32.12 | 33.2 | 34.52 | 35.84 | 37.16 | 38.48 | 39.8 | 41.64 | 43.48 | 45.32 | 47.16 | 49 | 51 | 53 | 55 | 57 | 59 | 61.32 | 63.64 | 65.96 | 68.28 | 70.6
13 | 2.2 | 13022 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 35.04 | 36.48 | 37.92 | 39.36 | 40.8 | 42.52 | 44.24 | 45.96 | 47.68 | 49.4 | 51.52 | 53.64 | 55.76 | 57.88 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72
13 | 2.4 | 13024 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6 | 36.04 | 37.48 | 38.92 | 40.36 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.6 | 54.8 | 57 | 59.2 | 61.4 | 63.8 | 66.2 | 68.6 | 71 | 73.4
13 | 2.6 | 13026 | 24.4 | 25.36 | 26.32 | 27.28 | 28.24 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.56 | 38.12 | 39.68 | 41.24 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 51.8 | 53.92 | 56.04 | 58.16 | 60.28 | 62.4 | 65 | 67.6 | 70.2 | 72.8 | 75.4
13 | 2.8 | 13028 | 25 | 25.96 | 26.92 | 27.88 | 28.84 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 45.12 | 47.04 | 48.96 | 50.88 | 52.8 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66.4 | 69 | 71.6 | 74.2 | 76.8
13 | 3 | 13030 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.12 | 48.04 | 49.96 | 51.88 | 53.8 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67.4 | 70 | 72.6 | 75.2 | 77.8
14 | 0 | 14000 | 17.6 | 18.44 | 19.28 | 20.12 | 20.96 | 21.8 | 22.52 | 23.24 | 23.96 | 24.68 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.72 | 39.04 | 40.36 | 41.68 | 43 | 44.72 | 46.44 | 48.16 | 49.88 | 51.6
14 | 0.2 | 14002 | 17.6 | 18.44 | 19.28 | 20.12 | 20.96 | 21.8 | 22.52 | 23.24 | 23.96 | 24.68 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.72 | 39.04 | 40.36 | 41.68 | 43 | 44.72 | 46.44 | 48.16 | 49.88 | 51.6
14 | 0.4 | 14004 | 17.6 | 18.44 | 19.28 | 20.12 | 20.96 | 21.8 | 22.52 | 23.24 | 23.96 | 24.68 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.72 | 39.04 | 40.36 | 41.68 | 43 | 44.72 | 46.44 | 48.16 | 49.88 | 51.6
14 | 0.6 | 14006 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4 | 38.92 | 40.44 | 41.96 | 43.48 | 45 | 46.76 | 48.52 | 50.28 | 52.04 | 53.8
14 | 0.8 | 14008 | 18.8 | 19.48 | 20.16 | 20.84 | 21.52 | 22.2 | 23.08 | 23.96 | 24.84 | 25.72 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.32 | 34.64 | 35.96 | 37.28 | 38.6 | 40.12 | 41.64 | 43.16 | 44.68 | 46.2 | 47.96 | 49.72 | 51.48 | 53.24 | 55
14 | 1 | 14010 | 19.6 | 20.28 | 20.96 | 21.64 | 22.32 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.52 | 29.64 | 30.76 | 31.88 | 33 | 34.32 | 35.64 | 36.96 | 38.28 | 39.6 | 41.16 | 42.72 | 44.28 | 45.84 | 47.4 | 49.36 | 51.32 | 53.28 | 55.24 | 57.2
14 | 1.2 | 14012 | 19.8 | 20.48 | 21.16 | 21.84 | 22.52 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6 | 28.88 | 30.16 | 31.44 | 32.72 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.2 | 53 | 54.8 | 56.6 | 58.4
14 | 1.4 | 14014 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.08 | 25.96 | 26.84 | 27.72 | 28.6 | 29.72 | 30.84 | 31.96 | 33.08 | 34.2 | 35.72 | 37.24 | 38.76 | 40.28 | 41.8 | 43.56 | 45.32 | 47.08 | 48.84 | 50.6 | 52.56 | 54.52 | 56.48 | 58.44 | 60.4
14 | 1.6 | 14016 | 20.8 | 21.48 | 22.16 | 22.84 | 23.52 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 30.08 | 31.36 | 32.64 | 33.92 | 35.2 | 36.72 | 38.24 | 39.76 | 41.28 | 42.8 | 44.56 | 46.32 | 48.08 | 49.84 | 51.6 | 53.6 | 55.6 | 57.6 | 59.6 | 61.6
14 | 1.8 | 14018 | 21 | 21.84 | 22.68 | 23.52 | 24.36 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 31.08 | 32.36 | 33.64 | 34.92 | 36.2 | 37.76 | 39.32 | 40.88 | 42.44 | 44 | 45.76 | 47.52 | 49.28 | 51.04 | 52.8 | 54.96 | 57.12 | 59.28 | 61.44 | 63.6
14 | 2 | 14020 | 21 | 21.88 | 22.76 | 23.64 | 24.52 | 25.4 | 26.44 | 27.48 | 28.52 | 29.56 | 30.6 | 31.76 | 32.92 | 34.08 | 35.24 | 36.4 | 38.12 | 39.84 | 41.56 | 43.28 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.16 | 58.32 | 60.48 | 62.64 | 64.8
14 | 2.2 | 14022 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.16 | 49.12 | 51.08 | 53.04 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66
14 | 2.4 | 14024 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8 | 33.12 | 34.44 | 35.76 | 37.08 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.2 | 50.2 | 52.2 | 54.2 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.2
14 | 2.6 | 14026 | 22.2 | 23.08 | 23.96 | 24.84 | 25.72 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.48 | 34.96 | 36.44 | 37.92 | 39.4 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49.36 | 51.32 | 53.28 | 55.24 | 57.2 | 59.6 | 62 | 64.4 | 66.8 | 69.2
14 | 2.8 | 14028 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.52 | 29.64 | 30.76 | 31.88 | 33 | 34.32 | 35.64 | 36.96 | 38.28 | 39.6 | 41.36 | 43.12 | 44.88 | 46.64 | 48.4 | 50.4 | 52.4 | 54.4 | 56.4 | 58.4 | 60.8 | 63.2 | 65.6 | 68 | 70.4
14 | 3 | 14030 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.68 | 36.16 | 37.64 | 39.12 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.4 | 53.4 | 55.4 | 57.4 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.4
15 | 0 | 15000 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
15 | 0.2 | 15002 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
15 | 0.4 | 15004 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
15 | 0.6 | 15006 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49
15 | 0.8 | 15008 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50
15 | 1 | 15010 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52
15 | 1.2 | 15012 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26.2 | 27.4 | 28.6 | 29.8 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.6 | 48.2 | 49.8 | 51.4 | 53
15 | 1.4 | 15014 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27 | 28 | 29 | 30 | 31 | 32.4 | 33.8 | 35.2 | 36.6 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55
15 | 1.6 | 15016 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56
15 | 1.8 | 15018 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 23.8 | 24.6 | 25.4 | 26.2 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 50 | 52 | 54 | 56 | 58
15 | 2 | 15020 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.6 | 36.2 | 37.8 | 39.4 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51 | 53 | 55 | 57 | 59
15 | 2.2 | 15022 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 52 | 54 | 56 | 58 | 60
15 | 2.4 | 15024 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53 | 55 | 57 | 59 | 61
15 | 2.6 | 15026 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.4 | 31.8 | 33.2 | 34.6 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63
15 | 2.8 | 15028 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.6 | 39.2 | 40.8 | 42.4 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64
15 | 3 | 15030 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.4 | 32.8 | 34.2 | 35.6 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65
16 | 0 | 16000 | 15.2 | 15.96 | 16.72 | 17.48 | 18.24 | 19 | 19.56 | 20.12 | 20.68 | 21.24 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.56 | 33.72 | 34.88 | 36.04 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6
16 | 0.2 | 16002 | 15.2 | 15.96 | 16.72 | 17.48 | 18.24 | 19 | 19.56 | 20.12 | 20.68 | 21.24 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.56 | 33.72 | 34.88 | 36.04 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6
16 | 0.4 | 16004 | 15.2 | 15.96 | 16.72 | 17.48 | 18.24 | 19 | 19.56 | 20.12 | 20.68 | 21.24 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.56 | 33.72 | 34.88 | 36.04 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6
16 | 0.6 | 16006 | 16.2 | 16.76 | 17.32 | 17.88 | 18.44 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.72 | 24.64 | 25.56 | 26.48 | 27.4 | 28.4 | 29.4 | 30.4 | 31.4 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.48 | 41.96 | 43.44 | 44.92 | 46.4
16 | 0.8 | 16008 | 16.2 | 16.76 | 17.32 | 17.88 | 18.44 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40 | 41.52 | 43.04 | 44.56 | 46.08 | 47.6
16 | 1 | 16010 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.72 | 25.64 | 26.56 | 27.48 | 28.4 | 29.56 | 30.72 | 31.88 | 33.04 | 34.2 | 35.56 | 36.92 | 38.28 | 39.64 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4
16 | 1.2 | 16012 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.92 | 26.04 | 27.16 | 28.28 | 29.4 | 30.56 | 31.72 | 32.88 | 34.04 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.16 | 45.72 | 47.28 | 48.84 | 50.4
16 | 1.4 | 16014 | 17.2 | 17.92 | 18.64 | 19.36 | 20.08 | 20.8 | 21.56 | 22.32 | 23.08 | 23.84 | 24.6 | 25.56 | 26.52 | 27.48 | 28.44 | 29.4 | 30.72 | 32.04 | 33.36 | 34.68 | 36 | 37.52 | 39.04 | 40.56 | 42.08 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2
16 | 1.6 | 16016 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.76 | 22.52 | 23.28 | 24.04 | 24.8 | 25.92 | 27.04 | 28.16 | 29.28 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.52 | 40.04 | 41.56 | 43.08 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2
16 | 1.8 | 16018 | 18 | 18.76 | 19.52 | 20.28 | 21.04 | 21.8 | 22.56 | 23.32 | 24.08 | 24.84 | 25.6 | 26.76 | 27.92 | 29.08 | 30.24 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.48 | 49.36 | 51.24 | 53.12 | 55
16 | 2 | 16020 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.88 | 34.36 | 35.84 | 37.32 | 38.8 | 40.36 | 41.92 | 43.48 | 45.04 | 46.6 | 48.48 | 50.36 | 52.24 | 54.12 | 56
16 | 2.2 | 16022 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 22.92 | 23.84 | 24.76 | 25.68 | 26.6 | 27.76 | 28.92 | 30.08 | 31.24 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.72 | 42.44 | 44.16 | 45.88 | 47.6 | 49.48 | 51.36 | 53.24 | 55.12 | 57
16 | 2.4 | 16024 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40 | 41.68 | 43.36 | 45.04 | 46.72 | 48.4 | 50.32 | 52.24 | 54.16 | 56.08 | 58
16 | 2.6 | 16026 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.92 | 30.24 | 31.56 | 32.88 | 34.2 | 35.52 | 36.84 | 38.16 | 39.48 | 40.8 | 42.52 | 44.24 | 45.96 | 47.68 | 49.4 | 51.48 | 53.56 | 55.64 | 57.72 | 59.8
16 | 2.8 | 16028 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.72 | 25.64 | 26.56 | 27.48 | 28.4 | 29.56 | 30.72 | 31.88 | 33.04 | 34.2 | 35.72 | 37.24 | 38.76 | 40.28 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8
16 | 3 | 16030 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.76 | 25.72 | 26.68 | 27.64 | 28.6 | 29.92 | 31.24 | 32.56 | 33.88 | 35.2 | 36.72 | 38.24 | 39.76 | 41.28 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.48 | 55.56 | 57.64 | 59.72 | 61.8
17 | 0 | 17000 | 14.4 | 15.12 | 15.84 | 16.56 | 17.28 | 18 | 18.52 | 19.04 | 19.56 | 20.08 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
17 | 0.2 | 17002 | 14.4 | 15.12 | 15.84 | 16.56 | 17.28 | 18 | 18.52 | 19.04 | 19.56 | 20.08 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
17 | 0.4 | 17004 | 14.4 | 15.12 | 15.84 | 16.56 | 17.28 | 18 | 18.52 | 19.04 | 19.56 | 20.08 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
17 | 0.6 | 17006 | 15.4 | 15.92 | 16.44 | 16.96 | 17.48 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.44 | 23.28 | 24.12 | 24.96 | 25.8 | 26.8 | 27.8 | 28.8 | 29.8 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8
17 | 0.8 | 17008 | 15.4 | 15.92 | 16.44 | 16.96 | 17.48 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.24 | 28.28 | 29.32 | 30.36 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.44 | 40.88 | 42.32 | 43.76 | 45.2
17 | 1 | 17010 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.44 | 24.28 | 25.12 | 25.96 | 26.8 | 27.92 | 29.04 | 30.16 | 31.28 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8
17 | 1.2 | 17012 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.64 | 24.68 | 25.72 | 26.76 | 27.8 | 28.92 | 30.04 | 31.16 | 32.28 | 33.4 | 34.76 | 36.12 | 37.48 | 38.84 | 40.2 | 41.72 | 43.24 | 44.76 | 46.28 | 47.8
17 | 1.4 | 17014 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.32 | 21.04 | 21.76 | 22.48 | 23.2 | 24.12 | 25.04 | 25.96 | 26.88 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.44 | 36.88 | 38.32 | 39.76 | 41.2 | 42.84 | 44.48 | 46.12 | 47.76 | 49.4
17 | 1.6 | 17016 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.72 | 21.44 | 22.16 | 22.88 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.44 | 37.88 | 39.32 | 40.76 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4
17 | 1.8 | 17018 | 17 | 17.72 | 18.44 | 19.16 | 19.88 | 20.6 | 21.32 | 22.04 | 22.76 | 23.48 | 24.2 | 25.32 | 26.44 | 27.56 | 28.68 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52
17 | 2 | 17020 | 17.4 | 18.04 | 18.68 | 19.32 | 19.96 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 31.16 | 32.52 | 33.88 | 35.24 | 36.6 | 38.12 | 39.64 | 41.16 | 42.68 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53
17 | 2.2 | 17022 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.84 | 22.68 | 23.52 | 24.36 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.64 | 40.28 | 41.92 | 43.56 | 45.2 | 46.96 | 48.72 | 50.48 | 52.24 | 54
17 | 2.4 | 17024 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.24 | 28.28 | 29.32 | 30.36 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.64 | 49.48 | 51.32 | 53.16 | 55
17 | 2.6 | 17026 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.44 | 28.68 | 29.92 | 31.16 | 32.4 | 33.64 | 34.88 | 36.12 | 37.36 | 38.6 | 40.24 | 41.88 | 43.52 | 45.16 | 46.8 | 48.76 | 50.72 | 52.68 | 54.64 | 56.6
17 | 2.8 | 17028 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.44 | 24.28 | 25.12 | 25.96 | 26.8 | 27.92 | 29.04 | 30.16 | 31.28 | 32.4 | 33.84 | 35.28 | 36.72 | 38.16 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6
17 | 3 | 17030 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.52 | 24.44 | 25.36 | 26.28 | 27.2 | 28.44 | 29.68 | 30.92 | 32.16 | 33.4 | 34.84 | 36.28 | 37.72 | 39.16 | 40.6 | 42.24 | 43.88 | 45.52 | 47.16 | 48.8 | 50.76 | 52.72 | 54.68 | 56.64 | 58.6
18 | 0 | 18000 | 13.6 | 14.28 | 14.96 | 15.64 | 16.32 | 17 | 17.48 | 17.96 | 18.44 | 18.92 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.28 | 30.36 | 31.44 | 32.52 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8
18 | 0.2 | 18002 | 13.6 | 14.28 | 14.96 | 15.64 | 16.32 | 17 | 17.48 | 17.96 | 18.44 | 18.92 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.28 | 30.36 | 31.44 | 32.52 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8
18 | 0.4 | 18004 | 13.6 | 14.28 | 14.96 | 15.64 | 16.32 | 17 | 17.48 | 17.96 | 18.44 | 18.92 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.28 | 30.36 | 31.44 | 32.52 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8
18 | 0.6 | 18006 | 14.6 | 15.08 | 15.56 | 16.04 | 16.52 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.16 | 21.92 | 22.68 | 23.44 | 24.2 | 25.2 | 26.2 | 27.2 | 28.2 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.24 | 37.48 | 38.72 | 39.96 | 41.2
18 | 0.8 | 18008 | 14.6 | 15.08 | 15.56 | 16.04 | 16.52 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.76 | 26.72 | 27.68 | 28.64 | 29.6 | 30.88 | 32.16 | 33.44 | 34.72 | 36 | 37.36 | 38.72 | 40.08 | 41.44 | 42.8
18 | 1 | 18010 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.16 | 22.92 | 23.68 | 24.44 | 25.2 | 26.28 | 27.36 | 28.44 | 29.52 | 30.6 | 31.88 | 33.16 | 34.44 | 35.72 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2
18 | 1.2 | 18012 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.36 | 23.32 | 24.28 | 25.24 | 26.2 | 27.28 | 28.36 | 29.44 | 30.52 | 31.6 | 32.84 | 34.08 | 35.32 | 36.56 | 37.8 | 39.28 | 40.76 | 42.24 | 43.72 | 45.2
18 | 1.4 | 18014 | 15.6 | 16.16 | 16.72 | 17.28 | 17.84 | 18.4 | 19.08 | 19.76 | 20.44 | 21.12 | 21.8 | 22.68 | 23.56 | 24.44 | 25.32 | 26.2 | 27.36 | 28.52 | 29.68 | 30.84 | 32 | 33.36 | 34.72 | 36.08 | 37.44 | 38.8 | 40.36 | 41.92 | 43.48 | 45.04 | 46.6
18 | 1.6 | 18016 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.68 | 20.36 | 21.04 | 21.72 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.36 | 35.72 | 37.08 | 38.44 | 39.8 | 41.36 | 42.92 | 44.48 | 46.04 | 47.6
18 | 1.8 | 18018 | 16 | 16.68 | 17.36 | 18.04 | 18.72 | 19.4 | 20.08 | 20.76 | 21.44 | 22.12 | 22.8 | 23.88 | 24.96 | 26.04 | 27.12 | 28.2 | 29.36 | 30.52 | 31.68 | 32.84 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.44 | 44.08 | 45.72 | 47.36 | 49
18 | 2 | 18020 | 16.6 | 17.16 | 17.72 | 18.28 | 18.84 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.44 | 30.68 | 31.92 | 33.16 | 34.4 | 35.88 | 37.36 | 38.84 | 40.32 | 41.8 | 43.44 | 45.08 | 46.72 | 48.36 | 50
18 | 2.2 | 18022 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.88 | 25.96 | 27.04 | 28.12 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.56 | 38.12 | 39.68 | 41.24 | 42.8 | 44.44 | 46.08 | 47.72 | 49.36 | 51
18 | 2.4 | 18024 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.76 | 26.72 | 27.68 | 28.64 | 29.6 | 30.88 | 32.16 | 33.44 | 34.72 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52
18 | 2.6 | 18026 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.96 | 27.12 | 28.28 | 29.44 | 30.6 | 31.76 | 32.92 | 34.08 | 35.24 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.04 | 47.88 | 49.72 | 51.56 | 53.4
18 | 2.8 | 18028 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.16 | 22.92 | 23.68 | 24.44 | 25.2 | 26.28 | 27.36 | 28.44 | 29.52 | 30.6 | 31.96 | 33.32 | 34.68 | 36.04 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.04 | 48.88 | 50.72 | 52.56 | 54.4
18 | 3 | 18030 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.28 | 23.16 | 24.04 | 24.92 | 25.8 | 26.96 | 28.12 | 29.28 | 30.44 | 31.6 | 32.96 | 34.32 | 35.68 | 37.04 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.04 | 49.88 | 51.72 | 53.56 | 55.4
19 | 0 | 19000 | 12.8 | 13.44 | 14.08 | 14.72 | 15.36 | 16 | 16.44 | 16.88 | 17.32 | 17.76 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4
19 | 0.2 | 19002 | 12.8 | 13.44 | 14.08 | 14.72 | 15.36 | 16 | 16.44 | 16.88 | 17.32 | 17.76 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4
19 | 0.4 | 19004 | 12.8 | 13.44 | 14.08 | 14.72 | 15.36 | 16 | 16.44 | 16.88 | 17.32 | 17.76 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4
19 | 0.6 | 19006 | 13.8 | 14.24 | 14.68 | 15.12 | 15.56 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 19.88 | 20.56 | 21.24 | 21.92 | 22.6 | 23.6 | 24.6 | 25.6 | 26.6 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.12 | 35.24 | 36.36 | 37.48 | 38.6
19 | 0.8 | 19008 | 13.8 | 14.24 | 14.68 | 15.12 | 15.56 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.28 | 25.16 | 26.04 | 26.92 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.28 | 36.56 | 37.84 | 39.12 | 40.4
19 | 1 | 19010 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 20.88 | 21.56 | 22.24 | 22.92 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6
19 | 1.2 | 19012 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 21.08 | 21.96 | 22.84 | 23.72 | 24.6 | 25.64 | 26.68 | 27.72 | 28.76 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.84 | 38.28 | 39.72 | 41.16 | 42.6
19 | 1.4 | 19014 | 14.8 | 15.28 | 15.76 | 16.24 | 16.72 | 17.2 | 17.84 | 18.48 | 19.12 | 19.76 | 20.4 | 21.24 | 22.08 | 22.92 | 23.76 | 24.6 | 25.68 | 26.76 | 27.84 | 28.92 | 30 | 31.28 | 32.56 | 33.84 | 35.12 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8
19 | 1.6 | 19016 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.64 | 19.28 | 19.92 | 20.56 | 21.2 | 22.08 | 22.96 | 23.84 | 24.72 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.28 | 33.56 | 34.84 | 36.12 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8
19 | 1.8 | 19018 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.84 | 19.48 | 20.12 | 20.76 | 21.4 | 22.44 | 23.48 | 24.52 | 25.56 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.92 | 41.44 | 42.96 | 44.48 | 46
19 | 2 | 19020 | 15.8 | 16.28 | 16.76 | 17.24 | 17.72 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.72 | 28.84 | 29.96 | 31.08 | 32.2 | 33.64 | 35.08 | 36.52 | 37.96 | 39.4 | 40.92 | 42.44 | 43.96 | 45.48 | 47
19 | 2.2 | 19022 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.68 | 20.36 | 21.04 | 21.72 | 22.4 | 23.44 | 24.48 | 25.52 | 26.56 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.48 | 35.96 | 37.44 | 38.92 | 40.4 | 41.92 | 43.44 | 44.96 | 46.48 | 48
19 | 2.4 | 19024 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.28 | 25.16 | 26.04 | 26.92 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.28 | 43.96 | 45.64 | 47.32 | 49
19 | 2.6 | 19026 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.48 | 25.56 | 26.64 | 27.72 | 28.8 | 29.88 | 30.96 | 32.04 | 33.12 | 34.2 | 35.68 | 37.16 | 38.64 | 40.12 | 41.6 | 43.32 | 45.04 | 46.76 | 48.48 | 50.2
19 | 2.8 | 19028 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 20.88 | 21.56 | 22.24 | 22.92 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.08 | 31.36 | 32.64 | 33.92 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.32 | 46.04 | 47.76 | 49.48 | 51.2
19 | 3 | 19030 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 21.04 | 21.88 | 22.72 | 23.56 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 31.08 | 32.36 | 33.64 | 34.92 | 36.2 | 37.68 | 39.16 | 40.64 | 42.12 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2
20 | 0 | 20000 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
20 | 0.2 | 20002 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
20 | 0.4 | 20004 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
20 | 0.6 | 20006 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36
20 | 0.8 | 20008 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38
20 | 1 | 20010 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 23 | 24 | 25 | 26 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39
20 | 1.2 | 20012 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40
20 | 1.4 | 20014 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41
20 | 1.6 | 20016 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42
20 | 1.8 | 20018 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43
20 | 2 | 20020 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.4 | 32.8 | 34.2 | 35.6 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44
20 | 2.2 | 20022 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32.4 | 33.8 | 35.2 | 36.6 | 38 | 39.4 | 40.8 | 42.2 | 43.6 | 45
20 | 2.4 | 20024 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46
20 | 2.6 | 20026 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
20 | 2.8 | 20028 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 23 | 24 | 25 | 26 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48
20 | 3 | 20030 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49
21 | 0 | 21000 | 11.2 | 11.76 | 12.32 | 12.88 | 13.44 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6
21 | 0.2 | 21002 | 11.2 | 11.76 | 12.32 | 12.88 | 13.44 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6
21 | 0.4 | 21004 | 11.2 | 11.76 | 12.32 | 12.88 | 13.44 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6
21 | 0.6 | 21006 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.36 | 17.92 | 18.48 | 19.04 | 19.6 | 20.52 | 21.44 | 22.36 | 23.28 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 29.76 | 30.72 | 31.68 | 32.64 | 33.6
21 | 0.8 | 21008 | 12.2 | 12.56 | 12.92 | 13.28 | 13.64 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4
21 | 1 | 21010 | 12.2 | 12.72 | 13.24 | 13.76 | 14.28 | 14.8 | 15.36 | 15.92 | 16.48 | 17.04 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4
21 | 1.2 | 21012 | 12.2 | 12.76 | 13.32 | 13.88 | 14.44 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.52 | 19.24 | 19.96 | 20.68 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 26.96 | 27.92 | 28.88 | 29.84 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4
21 | 1.4 | 21014 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.32 | 28.44 | 29.56 | 30.68 | 31.8 | 33.08 | 34.36 | 35.64 | 36.92 | 38.2
21 | 1.6 | 21016 | 13 | 13.56 | 14.12 | 14.68 | 15.24 | 15.8 | 16.36 | 16.92 | 17.48 | 18.04 | 18.6 | 19.36 | 20.12 | 20.88 | 21.64 | 22.4 | 23.32 | 24.24 | 25.16 | 26.08 | 27 | 28.12 | 29.24 | 30.36 | 31.48 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2
21 | 1.8 | 21018 | 13.2 | 13.72 | 14.24 | 14.76 | 15.28 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.68 | 20.56 | 21.44 | 22.32 | 23.2 | 24.16 | 25.12 | 26.08 | 27.04 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2
21 | 2 | 21020 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.32 | 30.64 | 31.96 | 33.28 | 34.6 | 35.88 | 37.16 | 38.44 | 39.72 | 41
21 | 2.2 | 21022 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.36 | 17.92 | 18.48 | 19.04 | 19.6 | 20.52 | 21.44 | 22.36 | 23.28 | 24.2 | 25.16 | 26.12 | 27.08 | 28.04 | 29 | 30.28 | 31.56 | 32.84 | 34.12 | 35.4 | 36.72 | 38.04 | 39.36 | 40.68 | 42
21 | 2.4 | 21024 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.52 | 18.24 | 18.96 | 19.68 | 20.4 | 21.16 | 21.92 | 22.68 | 23.44 | 24.2 | 25.32 | 26.44 | 27.56 | 28.68 | 29.8 | 30.96 | 32.12 | 33.28 | 34.44 | 35.6 | 37.08 | 38.56 | 40.04 | 41.52 | 43
21 | 2.6 | 21026 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.16 | 27.12 | 28.08 | 29.04 | 30 | 31.28 | 32.56 | 33.84 | 35.12 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8
21 | 2.8 | 21028 | 14.8 | 15.36 | 15.92 | 16.48 | 17.04 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8
21 | 3 | 21030 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.52 | 19.24 | 19.96 | 20.68 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 27.12 | 28.24 | 29.36 | 30.48 | 31.6 | 32.92 | 34.24 | 35.56 | 36.88 | 38.2 | 39.68 | 41.16 | 42.64 | 44.12 | 45.6
22 | 0 | 22000 | 10.4 | 10.92 | 11.44 | 11.96 | 12.48 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2
22 | 0.2 | 22002 | 10.4 | 10.92 | 11.44 | 11.96 | 12.48 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2
22 | 0.4 | 22004 | 10.4 | 10.92 | 11.44 | 11.96 | 12.48 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2
22 | 0.6 | 22006 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.12 | 16.64 | 17.16 | 17.68 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.52 | 28.44 | 29.36 | 30.28 | 31.2
22 | 0.8 | 22008 | 11.4 | 11.72 | 12.04 | 12.36 | 12.68 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.32 | 17.04 | 17.76 | 18.48 | 19.2 | 19.92 | 20.64 | 21.36 | 22.08 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8
22 | 1 | 22010 | 11.4 | 11.84 | 12.28 | 12.72 | 13.16 | 13.6 | 14.12 | 14.64 | 15.16 | 15.68 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.64 | 30.68 | 31.72 | 32.76 | 33.8
22 | 1.2 | 22012 | 11.4 | 11.92 | 12.44 | 12.96 | 13.48 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.24 | 17.88 | 18.52 | 19.16 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 24.92 | 25.84 | 26.76 | 27.68 | 28.6 | 29.84 | 31.08 | 32.32 | 33.56 | 34.8
22 | 1.4 | 22014 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.32 | 18.04 | 18.76 | 19.48 | 20.2 | 21.04 | 21.88 | 22.72 | 23.56 | 24.4 | 25.44 | 26.48 | 27.52 | 28.56 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4
22 | 1.6 | 22016 | 12 | 12.52 | 13.04 | 13.56 | 14.08 | 14.6 | 15.12 | 15.64 | 16.16 | 16.68 | 17.2 | 17.92 | 18.64 | 19.36 | 20.08 | 20.8 | 21.64 | 22.48 | 23.32 | 24.16 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4
22 | 1.8 | 22018 | 12.4 | 12.84 | 13.28 | 13.72 | 14.16 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.36 | 19.12 | 19.88 | 20.64 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4
22 | 2 | 22020 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 27.24 | 28.48 | 29.72 | 30.96 | 32.2 | 33.36 | 34.52 | 35.68 | 36.84 | 38
22 | 2.2 | 22022 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.12 | 16.64 | 17.16 | 17.68 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.32 | 24.24 | 25.16 | 26.08 | 27 | 28.16 | 29.32 | 30.48 | 31.64 | 32.8 | 34.04 | 35.28 | 36.52 | 37.76 | 39
22 | 2.4 | 22024 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.24 | 16.88 | 17.52 | 18.16 | 18.8 | 19.52 | 20.24 | 20.96 | 21.68 | 22.4 | 23.44 | 24.48 | 25.52 | 26.56 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40
22 | 2.6 | 22026 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.32 | 17.04 | 17.76 | 18.48 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.16 | 30.32 | 31.48 | 32.64 | 33.8 | 35.16 | 36.52 | 37.88 | 39.24 | 40.6
22 | 2.8 | 22028 | 13.6 | 14.12 | 14.64 | 15.16 | 15.68 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.84 | 31.08 | 32.32 | 33.56 | 34.8 | 36.16 | 37.52 | 38.88 | 40.24 | 41.6
22 | 3 | 22030 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.24 | 17.88 | 18.52 | 19.16 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 25.04 | 26.08 | 27.12 | 28.16 | 29.2 | 30.44 | 31.68 | 32.92 | 34.16 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
23 | 0 | 23000 | 9.6 | 10.08 | 10.56 | 11.04 | 11.52 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8
23 | 0.2 | 23002 | 9.6 | 10.08 | 10.56 | 11.04 | 11.52 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8
23 | 0.4 | 23004 | 9.6 | 10.08 | 10.56 | 11.04 | 11.52 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8
23 | 0.6 | 23006 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.88 | 15.36 | 15.84 | 16.32 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.28 | 26.16 | 27.04 | 27.92 | 28.8
23 | 0.8 | 23008 | 10.6 | 10.88 | 11.16 | 11.44 | 11.72 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 15.08 | 15.76 | 16.44 | 17.12 | 17.8 | 18.48 | 19.16 | 19.84 | 20.52 | 21.2 | 22.04 | 22.88 | 23.72 | 24.56 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2
23 | 1 | 23010 | 10.6 | 10.96 | 11.32 | 11.68 | 12.04 | 12.4 | 12.88 | 13.36 | 13.84 | 14.32 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.36 | 28.32 | 29.28 | 30.24 | 31.2
23 | 1.2 | 23012 | 10.6 | 11.08 | 11.56 | 12.04 | 12.52 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 15.96 | 16.52 | 17.08 | 17.64 | 18.2 | 18.96 | 19.72 | 20.48 | 21.24 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.56 | 28.72 | 29.88 | 31.04 | 32.2
23 | 1.4 | 23014 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.56 | 20.32 | 21.08 | 21.84 | 22.6 | 23.56 | 24.52 | 25.48 | 26.44 | 27.4 | 28.44 | 29.48 | 30.52 | 31.56 | 32.6
23 | 1.6 | 23016 | 11 | 11.48 | 11.96 | 12.44 | 12.92 | 13.4 | 13.88 | 14.36 | 14.84 | 15.32 | 15.8 | 16.48 | 17.16 | 17.84 | 18.52 | 19.2 | 19.96 | 20.72 | 21.48 | 22.24 | 23 | 23.96 | 24.92 | 25.88 | 26.84 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6
23 | 1.8 | 23018 | 11.6 | 11.96 | 12.32 | 12.68 | 13.04 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.48 | 21.36 | 22.24 | 23.12 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6
23 | 2 | 23020 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 25.16 | 26.32 | 27.48 | 28.64 | 29.8 | 30.84 | 31.88 | 32.92 | 33.96 | 35
23 | 2.2 | 23022 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.88 | 15.36 | 15.84 | 16.32 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.48 | 22.36 | 23.24 | 24.12 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.36 | 32.52 | 33.68 | 34.84 | 36
23 | 2.4 | 23024 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.96 | 15.52 | 16.08 | 16.64 | 17.2 | 17.88 | 18.56 | 19.24 | 19.92 | 20.6 | 21.56 | 22.52 | 23.48 | 24.44 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37
23 | 2.6 | 23026 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 15.08 | 15.76 | 16.44 | 17.12 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.48 | 23.36 | 24.24 | 25.12 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4
23 | 2.8 | 23028 | 12.4 | 12.88 | 13.36 | 13.84 | 14.32 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.56 | 28.72 | 29.88 | 31.04 | 32.2 | 33.44 | 34.68 | 35.92 | 37.16 | 38.4
23 | 3 | 23030 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 15.96 | 16.52 | 17.08 | 17.64 | 18.2 | 18.96 | 19.72 | 20.48 | 21.24 | 22 | 22.96 | 23.92 | 24.88 | 25.84 | 26.8 | 27.96 | 29.12 | 30.28 | 31.44 | 32.6 | 33.84 | 35.08 | 36.32 | 37.56 | 38.8
24 | 0 | 24000 | 8.8 | 9.24 | 9.68 | 10.12 | 10.56 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4
24 | 0.2 | 24002 | 8.8 | 9.24 | 9.68 | 10.12 | 10.56 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4
24 | 0.4 | 24004 | 8.8 | 9.24 | 9.68 | 10.12 | 10.56 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4
24 | 0.6 | 24006 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.64 | 14.08 | 14.52 | 14.96 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.48 | 20.16 | 20.84 | 21.52 | 22.2 | 23.04 | 23.88 | 24.72 | 25.56 | 26.4
24 | 0.8 | 24008 | 9.8 | 10.04 | 10.28 | 10.52 | 10.76 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.84 | 14.48 | 15.12 | 15.76 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.32 | 21.04 | 21.76 | 22.48 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6
24 | 1 | 24010 | 9.8 | 10.08 | 10.36 | 10.64 | 10.92 | 11.2 | 11.64 | 12.08 | 12.52 | 12.96 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.08 | 25.96 | 26.84 | 27.72 | 28.6
24 | 1.2 | 24012 | 9.8 | 10.24 | 10.68 | 11.12 | 11.56 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.68 | 15.16 | 15.64 | 16.12 | 16.6 | 17.28 | 17.96 | 18.64 | 19.32 | 20 | 20.84 | 21.68 | 22.52 | 23.36 | 24.2 | 25.28 | 26.36 | 27.44 | 28.52 | 29.6
24 | 1.4 | 24014 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.84 | 15.48 | 16.12 | 16.76 | 17.4 | 18.08 | 18.76 | 19.44 | 20.12 | 20.8 | 21.68 | 22.56 | 23.44 | 24.32 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8
24 | 1.6 | 24016 | 10 | 10.44 | 10.88 | 11.32 | 11.76 | 12.2 | 12.64 | 13.08 | 13.52 | 13.96 | 14.4 | 15.04 | 15.68 | 16.32 | 16.96 | 17.6 | 18.28 | 18.96 | 19.64 | 20.32 | 21 | 21.88 | 22.76 | 23.64 | 24.52 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8
24 | 1.8 | 24018 | 10.8 | 11.08 | 11.36 | 11.64 | 11.92 | 12.2 | 12.8 | 13.4 | 14 | 14.6 | 15.2 | 15.72 | 16.24 | 16.76 | 17.28 | 17.8 | 18.64 | 19.48 | 20.32 | 21.16 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8
24 | 2 | 24020 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 23.08 | 24.16 | 25.24 | 26.32 | 27.4 | 28.32 | 29.24 | 30.16 | 31.08 | 32
24 | 2.2 | 24022 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.64 | 14.08 | 14.52 | 14.96 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.64 | 20.48 | 21.32 | 22.16 | 23 | 23.92 | 24.84 | 25.76 | 26.68 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33
24 | 2.4 | 24024 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.68 | 14.16 | 14.64 | 15.12 | 15.6 | 16.24 | 16.88 | 17.52 | 18.16 | 18.8 | 19.68 | 20.56 | 21.44 | 22.32 | 23.2 | 24.24 | 25.28 | 26.32 | 27.36 | 28.4 | 29.52 | 30.64 | 31.76 | 32.88 | 34
24 | 2.6 | 24026 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.84 | 14.48 | 15.12 | 15.76 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 24.92 | 25.84 | 26.76 | 27.68 | 28.6 | 29.72 | 30.84 | 31.96 | 33.08 | 34.2
24 | 2.8 | 24028 | 11.2 | 11.64 | 12.08 | 12.52 | 12.96 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.28 | 26.36 | 27.44 | 28.52 | 29.6 | 30.72 | 31.84 | 32.96 | 34.08 | 35.2
24 | 3 | 24030 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.68 | 15.16 | 15.64 | 16.12 | 16.6 | 17.28 | 17.96 | 18.64 | 19.32 | 20 | 20.88 | 21.76 | 22.64 | 23.52 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4
25 | 0 | 25000 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23
25 | 0.2 | 25002 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23
25 | 0.4 | 25004 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23
25 | 0.6 | 25006 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24
25 | 0.8 | 25008 | 9 | 9.2 | 9.4 | 9.6 | 9.8 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25
25 | 1 | 25010 | 9 | 9.2 | 9.4 | 9.6 | 9.8 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26
25 | 1.2 | 25012 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27
25 | 1.4 | 25014 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 23.8 | 24.6 | 25.4 | 26.2 | 27
25 | 1.6 | 25016 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28
25 | 1.8 | 25018 | 10 | 10.2 | 10.4 | 10.6 | 10.8 | 11 | 11.6 | 12.2 | 12.8 | 13.4 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29
25 | 2 | 25020 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 21 | 22 | 23 | 24 | 25 | 25.8 | 26.6 | 27.4 | 28.2 | 29
25 | 2.2 | 25022 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30
25 | 2.4 | 25024 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
25 | 2.6 | 25026 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27 | 28 | 29 | 30 | 31
25 | 2.8 | 25028 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
25 | 3 | 25030 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Notes:
| 1. |  | 6: Table values were obtained by linear interpolation using CT values published in USEPA's Guidance Manual for Compliance with the Filtration and Disinfection
Requirements for Public Water Systems Using Surface Water Sources, March 1991 edition. This table was developed by Nancy Feagin, P.E. of the
Drinking Water Northwest Regional Office
| 2. |  | 6: For other levels of log inactivation, multiply the table values by the log inactivation required. For example, for 0.5 log inactivation multiply the table values by 0.5.
| 3. |  | 6: For systems with pH values exceeding 9.0 see the Interim Enhanced Surface Water Treatment Rule Notice of Data Availability, Federal Register, November 3, 1997.